## Slide 1: SISTEM DISTRIBUSI
ELECTRIC POWER DISTRIBUTION SYSTEM ENGINEERING
Turan Gönen University of Missouri a: Columbia
McGraw-Hill Book Company New York St. Louis San Francisco Auckland Bogota Hamburg Johannesburg London Madrid Mexico Montreal New Delhi Panama Paris São Paulo Singapore Sydney Tokyo Toronto

## Slide 2
DISTRIBUTION SYSTEM PLANNING AND AUTOMATION

## Slide 7
DISTRIBUTION SYSTEM PLANNING
System planning is essential to assure that the growing demand for electricity can be satisfied by distribution system additions which are both technically adequate and reasonably economical.
In the future, more than in the past, electric utilities will need a fast and economical planning tool to evaluate the consequences of different proposed alternatives and their impact on the rest of the system to provide the necessary economical, reliable, and safe electric energy to consumers.
The objective of distribution system planning is to assure that the growing demand for electricity, in terms of increasing growth rates and high load densities
FACTORS AFFECTING SYSTEM PLANNING
Load Forecasting
Substation Expansion
Substation Site Selection
primary voltage selection
number of feeders
conductor size selection
total cost

## Slide 9
LOAD FORECASTING

## Slide 10
A system performance analysis is done to determine whether the present system is capable of handling the new load increase with respect to the company’s criteria.
SYSTEM PERFORMANCE
This analysis, constituting the second stage of the process, requires the use of tools such as a distribution load flow program, a voltage profile, and a regulation program.
The acceptability criteria, representing the company’s policies, obligations to the consumers, and additional constraints can include:
Service continuity
The maximum allowable peak-load voltage drop to the most remote customer on the secondary
The maximum allowable voltage dip occasioned by the starting of a motor of specified starting current characteristics at the most remote point on the secondary
The maximum allowable peak load
Service reliability
Power losses

## Slide 11
SUBSTATION EXPANSION

## Slide 12
SUBSTATION SITE SELECTION

## Slide 13
Substation site selection procedure

## Slide 14
Other Factors
Once the load assignments to the substations are determined, then the remaining factors affecting primary voltage selection, feeder route selection, number of feeders, conductor size selection, and total cost

## Slide 15
DISTRIBUTION SYSTEM PLANNING IN THE FUTURE
Economic Factors
Demographic Factors
Technological Factors
FUTURE NATURE OF DISTRIBUTION PLANNING
Increasing Importance of Good Planning
Impacts of Load Management
The requirements of a successful load management program are specified by Delgado [19] as follows:
It must be able to reduce demand during critical system load periods
It must result in a reduction in new generation requirements, purchased power, and/or fuel costs.
It must have an acceptable cost/benefit ratio.
Its operation must be compatible with system design and operation.
It must operate at an acceptable reliability level.
It must have an acceptable level of customer convenience.
It must provide a benefit to the customer in the form of reduced rates or other incentives.
Cost/Benefit Ratio for Innovation
New Planning Tools

## Slide 16
THE CENTRAL ROLE OF THE COMPUTER IN DISTRIBUTION PLANNING

## Slide 17
IMPACT OF DISPERSED STORAGE AND GENERATION
Biomass Geothermal Pumped hydro Compressed air storage Solar thermal Photovoltaics Wind Fuel cells Storage battery Low-head hydro Cogeneration: Gas turbine Burning refuse Landfill gas

## Slide 18
DISTRIBUTION SYSTEM AUTOMATION
The motivating objectives of the DAC system are [25]:
1. Improved overall system efficiency in the use of both capital and energy 2. Increased market penetration of coal, nuclear, and renewable domestic energy sources 3. Reduced reserve requirements in both transmission and generation 4. Increased reliability of service to essential loads

## Slide 19
Applications of two-way radio communications. (From [30].)

## Slide 24
SUMMARY AND CONCLUSIONS
future distribution systems will be more complex than those of today, which means that the distribution system planner’s task will be more complex. If the systems being planned are to be optimal with respect to construction cost, capitalization, performance reliability, and operating efficiency, better planning and operation tools are required. While it is impossible to foresee all the effects that technology will have on the way in which distribution planning and engineering will be done, it is possible to identify the major forces which are beginning to institute a change in the methodology and extrapolate

## Slide 25
REFERENCES
Westinghouse Electric Corporation: Electric Utility Engineering Reference Book—Distribution Systems, vol. 3, East Pittsburgh, Pa, 1965
Energy Information Administration: Energy Data Reports—Statistics of Privately-Owned Electric Utilities in the United States, U.S. Department of Energy, 1975—1978.
The National Electric R’liability Study: Technical Study Reports, U.S. Department of Energy, DOE/EP-0005, Office of Emergency Operations, April 1981.
The National Power Grid Study, vol. 2, U.S. Department of Energy, DOE/ERA-0056-2, Economic Regulatory Administration, Office of Utility Systems, September 1979.
Gönen, T., et al.: “Toward Automated Distribution Systems Planning,” Proceedings of the IEEE Control of Power Systems Conference, Texas A&M University, College Station, Tex., Mar. 19—21, 1979, pp.23—30.
Munasinghe, M.: The Economics of Power System Reliability and Planning, Johns Hopkins, Baltimore, 1979.

## Slide 26
BASIC DEFINITIONS
LOAD CHARACTERISTICS
Demand “The demand of an installation or system is the load at the receiving terminals averaged over a specified interval of time” [1]
Here, the load may be given in kilowatts, kilovars, kilovoltamperes, kiloamperes, or amperes.
Demand interval It is the period over which the load is averaged
This selected ∆t period may be 15 min, 30 min, 1 hr, or even longer. Of course, there may be situations where the 15- and 30-min demands are identical.
The demand statement should express the demand interval ∆t used to measure it
Figure 2.1 shows a daily demand variation curve, or load curve, as a function of demand intervals.
The hour-to-hour load on a system changes over a wide range. For example, the daytime peak load is typically double the minimum load during the night. Usually, the annual peak load is, due to seasonal variations, about three times the annual minimum.
To calculate the average demand, the area under the curve has to be determined. This can easily be achieved by a computer program,

## Slide 27
Figure 2.1 A daily demand variation curve
The load is expressed in per unit (pu) of peak load of the system
The data given by the curve of Fig. 2-1 can also be expressed as shown in Fig. 2-2

## Slide 28
The curve is constructed by selecting the maximum peak points and connecting them by a curve.
This curve is called the load- duration curve
The load-duration curves can be daily, weekly, monthly, or annual. For example, if the curve is a plot of all the 8760 hourly loads during the year, it is called an annual load-duration curve.

## Slide 29
Maximum demand “The maximum demand of an installation or system is the greatest of all demands which have occurred during the specified period of time” [1].
The maximum demand statement should also express the demand interval used to measure it.
For example, the specific demand might be the maximum of all demands such as daily, weekly, monthly, or annual.
Example 2-1 Assume that the loading data given in Table 2-2 belongs to one of the primary feeders of the No Light & No Power (NL&NP) Company and that they are for a typical winter day.
Develop the idealized daily load curve for the given hypothetical primary feeder
SOLUTION The solution is self-explanatory, as shown in Fig. 2-3.
Diversified demand (or coincident demand) It is the demand of the composite group, as a whole, of somewhat unrelated loads over a specified period of time.
Here, the maximum diversified demand has an importance. It is the maximum sum of the contributions of the individual demands to the diversified demand over a specific time interval.
For example, “if the test locations can, in the aggregate, be considered statistically representative of the residential customers as a whole, a load curve for the entire residential class of customers can he prepared. If this same technique is used for other classes of customers, similar load curves can he prepared” [3].
As shown in Fig. 2-4,

## Slide 30
Figure 2-3
Time | Load, kW |  | 
 | Street lighting | Residential | Commercial
12 AM. | 100 | 200 | 200
1 | 100 | 200 | 200
2 | 100 | 200 | 200
3 | 100 | 200 | 200
4 | 100 | 200 | 200
5 | 100 | 200 | 200
6 | 100 | 200 | 200
7 | 100 | 300 | 200
8 | — | 400 | 300
9 | - | 500 | 500
10 | — | 500 | 1000
11 | — | 500 | 1000
12 noon | — | 500 | 1000
I | — | 500 | 1000
2 | — | 500 | 200
3 | — | 500 | 1200
4 | — | 500 | 1200
5 | 100 | 600 | 1200
6 | 100 | 700 | 800
7 | 100 | 800 | 400
8 | 100 | 1000 | 400
9 | 100 | 1000 | 400
10 | 100 | 800 | 200
11 | 100 | 600 | 200
l2PM | 100 | 300 | 200

## Slide 32
Noncoincident demand Manning [2] defines it as “the sum of the demands of a group of loads with no restrictions on the interval to which each demand is applicable.”
Here, again the maximum of the noncoincident demand is the value of some importance.
Demand factor It is the “ratio of the maximum demand of a system to the total connected load of the system” [1]. Therefore, the demand factor (DF) is
Connected load It is “the sum of the continuous ratings of the load-consuming apparatus connected to the system or any part thereof” [1].
When the maximum demand and total connected demand have the same units, the demand factor is dimensionless.
Utilization factor It is “the ratio of the maximum demand of a system to the rated capacity of the system” [1]. Therefore, the utilization factor (F) is

## Slide 33
Plant factor It is the ratio of the total actual energy produced or served over a designated period of time to the energy that would have been produced or served if the plant (or unit) had operated continuously at maximum rating.
It is also known as the capacity factor or the use factor. Therefore,
It is mostly used in generation studies. For example
or

## Slide 34
Load factor It is “the ratio of the average load over a designated period of time to the peak load occurring on that period” [I]. Therefore, the load factor FLD is
or
where T = time, in days, weeks, months, or years. The longer the period T is the smaller the resultant factor. The reason for this is that for the same maximum demand, the energy consumption covers a larger time period and results in a smaller average load. Here, when time T is selected to be in days, weeks, months, or years, use it in 24, 168, 730, or 8760 h, respectively. It is less than or equal to 1.0.
Therefore, for example, the annual load factor is

## Slide 35
Diversity factor It is “the ratio of the sum of the individual maximum demands of the various subdivisions of a system to the maximum demand of the whole system” [1]. Therefore, the diversity factor (Fr) is
or
or
where D1 = maximum demand of load i, disregarding time of occurrence
Dg = D1+2+3+ +n
= coincident maximum demand of group of n loads
The diversity factor can be equal to or greater than 1.0. From Eq. (2-1), the demand factor is

## Slide 36
or
Substituting Eq. (2-12) into Eq. (2-1 1), the diversity factor can also be given as
where
TCDi = total connected demand of group, or class, i load
DFi = demand factor of group, or class, i load
Coincidence factor It is “the ratio of the maximum coincident total demand of a group of consumers to the sum of the maximum power demands of individual consumers comprising the group both taken at the same point of supply for the same time” [1]. Therefore, the coincidence factor (Fe) is
or

## Slide 37
Thus, the coincidence factor is the reciprocal of diversity factor; that is,
These ideas on the diversity and coincidence are the basis for the theory and practice of north-to-south and east-to-west interconnections among the power pools in this country. For example, during wintertime, energy comes from south to north, and during summer, just the opposIte occurs. Also, east-to-west interconnections help to improve the energy dispatch by means of sunset or sunrise adjustments, i.e., the setting of clocks 1 h late or early.
Load diversity It is “the difference between the sum of the peaks of two or more individual loads and the peak of the combined load” [1]. Therefore, the load diversity (LD) is
Contribution factor Manning [2] defines ci as “the contribution factor of the ith load to the group maximum demand.” It is given in per unit of the individual maximum demand of the ith load. Therefore,

## Slide 38
Substituting Eq. (2-18) into Eq. (2-15),
or
Special cases Case1: D1=D2=D3=...=Dn=D. From Eq. (2-20),
or

## Slide 39
Case 2: c1 = c2 = c3 = ……. cn = c. Hence, from Eq. (2.20),
That is, the coincident factor is equal to the average contribution factor.
That is, the coincident factor i equal to the contribution factor
or
Loss-factor It is “the ratIo of the average power loss to the peak-load power loss during a specified period of time” [1]. Therefore, the loss factor (FLS) is
Equation (2.25) is applicable for the copper losses of the system but not for the iron losses.

## Slide 40
Example 2-2 Assume that annual peak load of a primary feeder is 2000 kW, at which the power loss, i.e., total copper, or I2R, loss, is 80 kW per three- phase. Assuming an annual loss factor of 0.15, determine: (a) The average annual power loss. (b) The total annual energy loss due to the copper losses of the feeder circuits.
SOLUTION (a) From Eq. (2-25), Average power loss = power loss at peak load x F LS = 80 kW x 0.15 =12kW
(b) The total annual energy loss is TAELCU = average power loss x 8760 h/yr = 12 x 8760 = 105,120 kWh

## Slide 41
Example 2-3 Assume that there are six residential customers connected to a distribution transformer, as shown in Fig. 2-5.
Assume that the connected load is 9 kW per house and that the demand factor and diversity factor for the group of six houses, either from the NL&NP Company’s records or from the relevant handbooks, have been decided as 0.65 and 1.10, respectively. Determine the diversified demand of the group of six houses on the distribution transformer DT427.
Notice the code in the customer account number, e.g., 4276. The first figure, 4, stands for feeder F4; the second figure, 2, indicates the lateral number connected to the F4 feeder; the third figure, 7, is for the distribution transformer on that lateral; and finally the last figure, 6, is for the house number connected to that distribution transformer.

## Slide 42
SOLUTION From Eq. (2-13), the diversified demand of the group on the distribution transformer is
Example 2-4 Assume that feeder 4 of Example 2-3 has a system peak of 3000 kVA per phase and a copper loss of 0.5 percent at the system peak. Determine the following: (a) The copper loss of the feeder in kilowatts per phase. (b.) The total copper losses of the feeder in kilowatts per three-phase.
SOLUTION (a) The copper loss of the feeder in kilowatts per phase is I2R ≈ 0.5% x system peak = 0.005 x 3200 kVA = 15 kW per phase

## Slide 43
(b) The total copper losses of the feeder in kilowatts per three-phase is
3I2R = 3 x 15 = 45 kW per three-phase
ExampLe 2-5 Assume that there are two primary feeders supplied by one of the three transformers located at the NL&NP’s Riverside distribution substation, as shown in Fig. 2-6.

## Slide 44
One of the feeders supplies an industrial load which occurs primarily between S A.M. and 11 P.M., with a peak of 2000 kW at 5 P.M. The other one feeds residential loads which occur mainly between 6 A.M. and 12 P.M., with a peak of 2000 kW at 9 P.M., as shown in Fig. 2-7.
Determine the following: (a) The diversity factor of the load connected to transformer T3. (b) The load diversity of the load connected to transformer T3. (c) The coincidence factor of the load connected to transformer T3

## Slide 45
SOLUTION (a) From Eq. (2-11) the diversity factor of the load is
(b) From Eq. (2-17), the load diversity of the load is
(c) From Eq. (3-16), the coincidence factor of the load is

## Slide 46
Example 2-6 Use the data given in Example 2-1 for the NL&NP’s load curve. Note that the peak occurs at 5 P.M. Determine the following: (a) The class contribution factors for each of the three load classes. (b) The diversity factor for the primary feeder. (c) The diversified maximum demand of the load group. (d) The coincidence factor of the load group.
SOLUTION (a) The class contribution factor is
For street lighting, residential, and commercial loads,

## Slide 47
(b) From Eq. (2-11), the diversity factor is
and from Eq. (2-18),
Substituting Eq. (2-18) into Eq. (2-11),
Therefore, the diversity factor for the primary feeder is

## Slide 50
THE RELATIONSHIP BETWEEN THE LOAD AND LOSS FACTORS
In general, the loss factor cannot be determined from the load factor. However, the limiting values of the relationship can be found [2]. Assume that the primary feeder shown in Fig. 2-8 is connected to a variable load.
Figure 2-9 shows an arbitrary and idealized load curve. However, it does not represent a daily load curve. Assume that the off-peak loss is P at some off-peak load P1 and that the peak loss is P2 at the peak load P2. The load factor is

## Slide 51
From Fig. 2-9,

## Slide 52
Substituting Eq. (2-27) into Eq. (2-26),
or
The loss factor is
where
P = average power loss P LS, max = maximum power loss P2 = peak loss at peak load

## Slide 53
From Fig. 2-9,
Substituting Eq. (2-30) into Eq. (2-29),
where
PLS,1 = off-peak loss at off-peak load t = peak load duration T = t = off-peak load duration
The copper losses are the function of the associated loads. Therefore, the off-peak and peak loads can be expressed, respectively, as
and

## Slide 54
where the k is a constant. Thus, substituting Eqs. (2-32) and (2-33) into Eq. (2-31), the loss factor can be expressed as
or
By using Eqs. (2-28) and (2-35), the load factor can be related to loss factor for three different cases:
Case 1: Off-peak load is zero. Here,
since P1 = 0. Therefore, from Eqs. (2-28) and (2-35),
That is, the load factor is equal to the loss factor and they are equal to the t/T constant.

## Slide 56
That is, the value of the loss factor approaches the value of the load factor. Therefore, in general, the value of the loss factor is
Therefore the loss factor cannot be determined directly from the load factor. The reason is that the loss factor is determined from losses as a function of time, which, in turn, are proportional to the time function of the square load [2—4].
However, Buller and Woodrow [5] developed an approximate formula to relate the loss factor to the load factor as
where
FLS = loss factor, pu
FLD load factor, pu
Equation (2-40) gives a reasonably close result. Figure 2-10 gives three different curves of loss factor as a function of load factor.

## Slide 58
Example 2-7 Assume that the Riverside distribution substation of the NL&NP Company supplying Ghost Town, which is a small city, experiences an annual peak load of 3500 kW. The total annual energy supplied to the primary feeder circuits is 10,000,000 kWh. The peak demand occurs in July or August and is due to air-conditioning load. (a) Find the annual average power demand. (b) Find the annual load factor.
SOLUTION Assume a monthly load curve as shown in Fig. 2-11

## Slide 59
(a) The annual average power demand is
(b) From Eq. (2-6), the annual load factor is
or, from Eq. (2-8),
The unsold energy, as shown in Fig. 2-11, is a measure of capacity and investment cost. Ideally, it should be kept at a minimum.

## Slide 60
Example 2-8 Use the data given in Example 2-6 and suppose that a new load of 100 kW with 100 percent annual load factor is to be supplied from the Riverside substation. The investment cost, or capacity cost, of the power system upstream, i.e., toward the generator, from this substation is 53.007kW per month. Assume that the energy delivered to these primary feeders costs the supplier, that is, NL&NP, $0.03/kWh. (a) Find the new annual load factor on the substation. (b) Find the total annual cost to NL&NP to serve this load.
SOLUTION
Figure 2-12 shows the new load curve after the addition of the new load of 100 kW with 100 percent load
(a) The new annual load factor on the substation is

## Slide 63
Example 2-9 Assume that the annual peak-load input to a primary feeder is 2000 kW. A computer program which calculates voltage drops and 12R losses shows that the total copper loss at the time of peak load is 12R 100 kW. The total annual energy supplied to the sending end of the feeder is 5.61 x 106 kwh. (a) By using Eq. (2.40), determine the annual loss factor. (b) Calculate the total annual copper loss energy and its value at $0.03/kwh.
SOLUTION (a) From Eq. (2-40), the annual loss factor is

## Slide 65
Example 2-10 Assume that one of the distribution transformers of the Riverside substation supplies three primary feeders. The 30-mm annual maximum demands per feeder are listed in the following table, together with the power factor (PF) at the time of annual peak load.
Assume a diversity factor of 1.15 among the three feeders for both real power (P) and reactive power (Q).
Feeder | Demand, kW | PF
1 | 1800 | 0.95
2 | 2000 | 0.85
3 | 2000 | 0.90
(a) Calculate the 30-mm annual maximum demand on the substation transformer in kilowatts
and in kilovoltamperes.
(b) Find the load diversity in kilowatts. (c) Select a suitable substation transformer size if zero load growth is expected and if
company policy permits as much as 25 percent short-time overloads on the distribution
substation transformers. Among the standard three- phase (3I) transformer sizes available are 2500/3125 kVA self-cooled/forced-air-cooled 3750/4687 kVA self-cooled/forced-air-cooled 5000/6250 ICVA self-cooled/forced-air-cooled 7500/9375 kVA self-cooled/forced-air-cooled

## Slide 66
(d) Now assume that the substation load will increase at a constant percentage rate per year
and will double in 10 years. If the 7599/9375-k VA-rated transformer is installed, in how
many years will it be loaded to its fans-on rating?
SOLUTION (a) From Eq. (2-10),

## Slide 69
MAXIMUM DIVERSIFIED DEMAND
Arvidson [7] developed a method of estimating distribution transformer loads in residential areas by the diversified-demand method which takes into account the diversity between similar loads and the noncoincidence of the peaks of different types of loads.
To take into account the noncoincidence of the peaks of different types of loads, Arvidson introduced the hourly variation factor. It is “the ratio of the demand of a particular type of load coincident with the group maximum demand to the maximum demand of that particular type of load [2].”
Table 2-3 gives the hourly variation curves for varidüs types of household appliances.
Figure 2-13 shows a number of curves for various types of household appliances to determine the average maximum diversified demand per customer in kilowatts per load. In Figure 2-13, each curve represents a 100 percent saturation level for a specific demand.
To apply Arvidson’s method to determine the maximum diversified demand for a given saturation level and appliance, the following steps are suggested [2]:
2. Read the corresponding diversified demand per customer from the curve, in Fig. 2-13, for the
given number of appliances.
1. Determine the total number of appliances by multiplying the total number of customers by the
per unit saturation.
3. Determine the maximi.im demand, multiplying the demand found in step 2 by the
total.number of appliances.
4. Finally, determine the contribution of that type load to the group maximum demand by
multiplying the resultant value from step 3 by the càrresponding hourly variation factor found
from Table 2-3.

## Slide 72
Example 2-11 Assume a typical distribution transformer (DT) that serves six residential loads, i.e., houses, through six service drops (SD) and two spans of secondary line (SL). Suppose that there are a total of 150 distribution transformers and 900 residences supplied by this primary feeder. Use Fig. 2-13 and Table 2-3. For the sake of illustration, assume that a typical residence contains a clothes dryer, a range, a refrigerator, and some lighting and miscellaneous appliances. Determine the following: (a) The 30-mm maximum diversified demand on the distribution transformer. (b) The 30-mm maximum diversified demand on the entire feeder. (c) Use the typical hourly variation factors given in Table 2-3 and calculate the small portion of the
daily demand curve on the distribution transformer, i.e., the total hourly diversified demands
at 4, 5, and 6 P.M., on the distribution transformer, in kilowatts.
SOLUTION (a) To determine the 30-mm maximum diversified demand on the distribution transformer,
the average maximum diversified demand per customer is
found from Fig. 2-13.
Therefore, when the number of loads is six, the average maximum diversified demands per customer are 1.6 kW/house for dryer 0.8 kW/house for range Pav,max 0.066 kW/house for refngerator 0.61 kW/house for lighting and misc. appliances Thus, the contributions of the appliances to the 30-miri maximum diversified demand on the distribution transformer is approximately 18.5 kW.

## Slide 73
(b) As in part a, the average maximum diversified demand per customer is found from Fig. 2-13.
Therefore, when the number of loads is 900 (note that, due to the given curve characteristics,
the answers would be the same as the ones for the number of loads of 100), then the average
maximum diversified demands per customer are
1.2 kW/house for dryer 0.53 kW/house for range Pav, mix 0.52 kW/house for refrigerator 0.044 kW/house for lighting and misc, appliance

## Slide 74
(c) From Table 2-3, the hourly variation factors can be found as 0.38, 0.24, 0.90, and 0.32 for
dryer, range, refrigerator, and lighting and miscellaneous appliances. Therefore, the total
hourly diversified demands on the distribution transformer can be calculated as given in
the following table. Note that the results given in col. 6 are the sum of the values given in
cols. 2 to 5.
Time (1) | Contributions to dcmand by |  |  |  | Total hourly diversified demand, kW (6)
 | Dryers, kW (2) | Ranges, kW (3) | Refrigerators, kW (4) | Lighting & misc. appliances, kW (5) | 
4 P.M | 9.6 x 0.38 | 4.8 x 0.24 | 0.4 x 0.90 | 3.7 x 0.32 | 6.344
5P.M. | 9.6 x 0.30 | 4.8 x 0.80 | 0.4 x 0.90 | 3.7 x 0.70 | 9.670
6 P.M. | 9.6 x 0.22 | 4.8 x 1.00 | 0.4 x 0.90 | 3.7 x 0.92 | 10.674

## Slide 75
LOAD GROWTH
The load growth of the geographical area served by a utility company is the most important factor influencing the expansion of the distribution system. Therefore, forecasting of load increases is essential to the planning process.
Fitting trends after transformation of data is a common practice in technical forecasting. An arithmetic straight line that will not fit the original data may fit, for example, the logarithms of the data as typified by the exponential trend
where Pn = load at the end of the nth year P0 = initial load g = annual growth rate n = number of years
This expression is sometimes called a growth equation, since it is often used to explain the phenomenon of growth through time. For example, if the load growth rate is known, the load at the end of the nth year is given by
Now, if it is set so that Pn = y, P0 = a, 1 + g = b, and n = x, then Eq. (2-42) is identical to the exponential trend equation (2-41). Table 2-4 gives a computer program to forecast the future demand values if the past demand values are known

## Slide 77
RATE STRUCTURE
Public utilities are monopolies, i.e., they have the exclusive right to sell their product in a given area. Their rates are subject to government regulation. The total revenue which a utility may be authorized to collect through the sales of its services should be equal to the company’s total cost of service. Therefore
The determination of the revenue requirement is a matter of regulatory commission decision. Therefore, designing schedules of rates which will produce the revenue requirement is a management responsibility subject to commission review. However, a regulatory commission cannot guarantee a specific rate of earnings; it can only declare that a public utility has been given the opportunity to try to earn it.
The rate of return is partly a function of local conditions and should correspond with the return being earned by comparable companies with similar risks. It should be sufficient to permit the utility to maintain its credit and attract the capital required to perform its tasks.
However, the rate schedules, by law, should avoid unjust and unreasonable discrimination, i.e., customers using the utility’s service under sirñilar conditions should be billed at similar prices.

## Slide 78
Of course, it is a matter f necessity to categorize the customers into classes and subclasses, but all customers in a given class should• be treated the same. There are several types of rate structures used by the utilities, and some of them are:
1. Flat demand rate structure
2. Straight-line meter rate structure
3. Block meter rate structure
6. Time-of-day (or peak-load pricing) structure
4. Demand rate structure
5. Season rate structure
The flat rate structure provides a constant price per kilowatthour which does not change with the time of use, season, or volume. The rate is negotiated knowing connected load; thus metering is not required. It is sometimes used for parking lot or street lighting service.
The straight-line meter rate structure is similar to the flat structure. It provides a single price per kilowauhour without considering customer demand costs.
The block meter rate structure provides lower prices for greater usage, i.e., it gives certain prices per kilowatthour for various kilowatthour blocks where the price per kilowatthour decreases for succeeding blocks.
Theoretically, it does not encourage energy conservation and off-peak usage. Therefore it causes a greater than necessary peak and, consequently, excess idle generation capacity during most of the time, resulting in higher rates to compensate the cost of a greater peak load capacity.

## Slide 79
The demand rate structure recognizes load factor and consequently provides separate charges for demand and energy. It gives either a constant price per kilowatthour consumed or a decreasing price per kilowatthour for succeeding blocks of energy used.
The seasonal rate structure specifies higher prices per kilowatthour used during the season of the year in which the system peak occurs (on-peak season) and lower prices during the season of the year in which the usage is the lowest (off-peak season).
The seasonal rate structure and the time-of-day rate structure are both designed to reduce the system’s peak load and therefore reduce the system’s idle stand-by capacity.
The time-of-day rate structure (or peak-load pricing) is similar to the seasonal load rate structure. It specifies higher prices per kilowatthour used during the peak- period of the day and lower prices during the off-peak period of the day.
Customer Billing
Customer billing is done by taking the difference in readings of the meter at two successive times, usually at an interval of 1 month. The difference in readings indicates the amount of electricity, in kilowatthours, constimed by the customer in that period. This amount is multiplied by the appropriate rate or the series of rates and the adjustment factors, and the bill is sent to the customer.
Figure 2-14 shows a typical monthly bill rendered to a residential customer. The monthly bill includes the following items in the indicated spaces:

## Slide 82
4. Date on which the billing period ended.
1. The customer’s account number.
2. A code showing which of the rate schedules was applied to the customer’s bill.
3. A code showing whether the customer’s bill was estimated or adjusted.
5. Number of kilowatthours the customer’s meter registered when the bill was tabulated.
6. Itemized list of charges. In this case, the only charge shown in box 6 of Fig. 2-14 is a figure
determined by adding the price of the electricity the customer has used to the routine taxes and
surcharges. However, had the customer received some special service during this billing
period, a service charge would appear in this space as a separate entry.
7. Information appears in this box only when the bill is sent to a nonresidential customer using
more than 6000 kWh electricity a month.
8. The number of kilowatthours the customer used during the billing period.
9. Total amount that the customer owes. 10. Environmental surcharge. 11. County energy tax. 12. State sales tax. 13. Fuel cost adjustment. Both the total adjustment and the adjustment per kilowatthour are
shown.

## Slide 83
14. Date on which bill, if unpaid, becomes overdue. 15. Amount due now. 16. Amount that the customer must pay if the bill becomes overdue.
The sample electrical bill, shown in Fig. 2-14 is based on the following rate schedule. Note that there is a minimum charge regardless of how little electricity the customer uses, and that the first 20 kWh that the customer uses is covered by this flat rate. Included in the minimum, or service, charge is the cost of providing service to the customer, including metering, meter reading, billing, and various overhead expenses.

## Slide 84
The sample bill shows a consumption of 2200 kWh which has been billed according to the following schedule:
The customer is billed according to the utility company’s rate schedule. In general, the rates vary according to the season. In most areas the demand for electricity increases in the warm months. Therefore, to meet the added burden, electric utilities are forced to use spare generators that are often less efficient and consequently more expensive to run. As an example, Table 2-5 gives a typical energy rate schedule for the on-peak and off-peak seasons for commercial users.

## Slide 85
Fuel Cost Adjustment
The rates stated previously are based upon an average cost, in dollars per million Btu, for the cost of fuel burned at the NL&NP’s thermal generating plants. The monthly bill as calculated under the previously stated rate is increased or decreased for each kilowatthour consumed by an amount calculated according to the following formula:
where FCAF = fuel cost adjustment factor, S/kwh, to be applied per kilowatthour consumed
A = weighted average Btu per kilowatthour for net generation from the NL&NP’s
thermal plants during the second calendar month preceding the end of the billing
period for which the kilowatthour usage is billed B = amount by which average cost of fuel per million Btu during the second calendar
month preceding the end of the billing period for which the kilowatthour usage is
billed exceeds or is less than Si/million Btu C = ratio, given in decimal, of the total net generation from all the NL&NP’s thermal
plants during the second calendar month preceding the end of the billing period for
which the kilowatthour usage is billed to the total net generation from all the
N&NP’s plants including hydro generation owned by the NL&IP, or kilowatthours
produced by hydro generation and purchased by the NL&NP, during the same period D = loss factor, which is the ratio, given in decimal, of kilowatthour losses (total
kilowatthour losses less losses of 2.5 percent associated with off-system sales) to net
system input, i.e., total system input less total kilowatthours in off-system sales, for
the year ending December 31 preceding. This ratio is updated every year and
applied for 12 months.

## Slide 86
Example 2-12 Assume that the NL&NP Utility Company has the following, and typical, commercial rate schedule. 1. Monthly billing demand = 30-mm monthly maximum kilowatt demand multiplied by the ratio
of (0.85 ÷ monthly average PF). The PF penalty shall not be applied when the consumer’s
monthly average PF exceeds 0.85. 2. Monthy demand charge = 52.001kW of monthly billing demand. 3. Monthly energy charges shall be: 2.50 cents/kWh for first 1000 kWh 2.00 cents/kWh for next 3000 kWh 1.50 cents/kWh for all kWh in excess of 4000
4. The total monthly charge shall be the sum of the monthly demand charge and the monthly
energy charge.
Assume that two consumers, as shown in Fig. 2-15, each requiring a distribution transformer, are supplied from a primary line of the NL&NP.
(a) Assume that an average month is 730 h and find the monthly load factor of each consumer.
(b) Find a reasonable size, i.e., continuous kilovoltampere rating, for each distribution
transformer.
(c) Calculate the monthly bill for each consumer.
(d) It is not uncommon to measure the average monthly PF on a monthly energy basis, where
both kilowatthours and kilovarhours are measured. On this basis, what size capacitor, in
kilovars, would raise the PF of customer B to 0.85?

## Slide 88
SOLUTION
(a) From Eq. (2-7), the monthly load factors for each consumer are the following. For customer A,
and for customer B,

## Slide 95
ELECTRIC METER TYPES
Figure 2-16 shows a single-phase watthour meter
An electric meter is the device used to measure the electricity sold by the electric utility company. It is not only used to measure the electric energy delivered to residential, commercial, and industrial customers but also used to measure the electric energy passing through various parts of the generation, transmission, and distribution systems.

## Slide 96
Fig. 2-17 shows its basic parts

## Slide 97
Fig. 2-18 gives a diagram of a typical motor and magnetic retarding system
for a single-phase watthour meter.

## Slide 98
The magnetic retarding system causes the rotor disk to establish, in combination with the stator, the speed at which the shaft will turn for a given load condition to determine the watthour constant.
Figure 2-19a shows a typical socket-mounted two-stator polyphase watthour meter. It is a combination of single-phase watthour meter stators that drive a rotor at a speed proportional to the total power in the circuit.

## Slide 99
The watthour meters employed to measure the electric energy passing through various parts of the generation, transmission, and distribution systems are required to measure large quantities of electric energy at relatively high voltages. For those applications, transformer-rated meters are developed.
They are used in conjunction with standard instrument transformers, i.e., current transformers (CT) and potential transformers (PT). These transformers reduce the voltage and the current to values that are suitable for the low-voltage and low-current meters.
Figure 2-19b shows a typical transformer-rated meter.

## Slide 100
Figure 2-20 shows a singlephase, two-wire watthour meter connected to a high-voltage circuit through current and potential transformers.

## Slide 101
A demand meter is basically a watthour meter with a timing element added. The meter functions as an integrator and adds up the kilowatthours of energy used in a certain time interval, for example, 15, 30, or 60 mm. Therefore, the demand meter indicates energy per time interval, or average power, which is expressed in kilowatts.
Figure 2-21 shows a demand register.

## Slide 102
Reading Electric Meters
Figure 2-22 shows a conventional dial-type register. To interpret it, read the dials from left to right. (Note that numbers run clockwise on some dials and counterclockwise on others.) The figures above each dial show how many kilowatthours are recorded each time the pointer makes a complete revolution.
By reading the register, i.e., the revolution counter, the customers’ bills can be determined. There are primarily two different types of registers: (1) conventional dial and (2) cyclometer.
As shown in Fig. 2-22, if the pointer is between numbers, read the smaller one. The 0 stands for 10. If the pointer is pointed directly at a number, look at the dial to the right. If that pointer has not yet passed 0, record the smaller number; if it has passed 0, record the number the pointer is on. For example, in Fig. 2-22, the pointer-on the first dial is between 8 and 9; therefore read 8.

## Slide 103
The pointer on the second dial is between 3 and 4; thus read 3. The pointer on the third dial is almost directly on 8, but the dial on the right has not reached 0 so the reading on the third dial is 7. The fourth dial is read 8. Therefore the total reading is 8378 kWh. The third dial would be read as S after the pointer on the 10-kWh dial reaches 0. This reading is based on a cumulative total; i.e., since the meter was last set at 0, 8378 kWh of electricity has been used.
To find the customer’s monthly use, take two readings I month apart, and subtract the earlier one from the later one. Some electric meters have a constant, or multip!ier, indicated on the meter. This type of meter is primarily for high- usage customers.
Figure 2-23 shows a cyclometer-type register. Here, even though the procedure is the same as in the conventional type, the wheels, which indicate numbers directly, replace the dials. Therefore, it makes possible the reading of the meter simply and directly, from left to right.

## Slide 104
Instantaneous Load Measurements Using Watthour Meters
The instantaneous kilowatt demand of any customer may be determined by making field observations of the kilowatthour meter serving the customer. However, the instantaneous load measurement should not replace demand meters that record for longer time intervals. The instantaneous demand may be detetmined by using one of the following equations: 1. For a self-contained watthour meter,
2. For a transformer-rated meter (where instrument transformers a watthour meter),
where D, = instantaneous demand, kW K = number of meter disk revolutions for a given time period
K,, = watthour meter constant (given on the register), Wh/rev T = time, s TR = current transformer ratio PTR = potential transformer ratio
Since the kilowatt demand is based on a short-time interval, two or more demand intervals should be measured. The average value of these demands is a good estimate of the given customer’s kilowatt demand during the intervals measured.

## Slide 105
Example 2-13 Assume that the load is measured twice with a watthour meter which has a meter constant of 7.2 and the following data are obtained:
Determine the instantaneous demands and the average demand
SOLUTION
From Eq. (2-45), for the first reading,
 | First reading | Second reading
Revolutions of disk | 32 | 27
Time interval for revolutions of disks | 59 | 40
and for the second reading,

## Slide 106
Therefore the average demand is
Example 2-14
Assume that the data given in Example 2-13 are the results of load measurement with watthour meters and instrument transformers. Suppose that the new meter constant is 1.8 and that the ratios of the current and potential transformers used are 200 and 1, respectively. Determine the instantaneous demands for both readings and the average demand.
SOLUTION
Therefore, from Eq. (2-46),

## Slide 107
and
Thus the average demand is
Example 2-15 Assume that the load is measured with watthour and varhour meters and instrument transformers and that the following readings are obtained:

## Slide 108
Assume that the new meter constants are 1.2 and that the ratios of the current and potential transformers used are 80 and 20, respectively. Determine the followixig: (a) The instantaneous kilowatt demands. (b) The average kilowatt demand. (c) The instantaneous kilovar demands (d) The average kilvar dem’and. (e) The average kilovoltampere demand.

## Slide 118
APPLICATION OF
DISTRIBUTION
TRANSFORMERS

## Slide 119
INTRODUCTION
In general, distribution transformers are used to reduce primary-system voltages voltages (2.4 to 34.5 kV) to utilization voltages (120 to 600 V).
Table 3-1 gives standard transformer capacity and voltage ratings according to ANSI Standard C57.12.20-1964 for single-phase distribution transformers.
The three primary symbols used are the dash (—), the slant (/), and the cross (x). The dash (—) is used to separate voltages of different windings, the slant (/) is used to separate voltages of the same winding, and the cross (x) is used to indicate a series-multiple connection.
Other voltages are also available, for example, 2400 x 7200, which is used on a 2400-V system that is to be changed later to 7200 V.
Secondary symbols used are the letter Y, which indicates that the winding is connected or may be connected wye, and Gnd Y, which indicates that the winding has one end grounded to the tank or brought out through a reduced insulation bushing. Windings that are delta-connected or may be connected delta are designated by the voltage of the winding only. In Table 3-1 further information is given by the order in which the voltages are written for low-voltage windings. To designate a winding with a mid-tap which will provide half the full-winding kilovoltampere rating at half the full-winding voltage, the full-winding voltage is written first, followed by a slant, and then the mid-tap voltage. For example, 240/120 is used for a three-wire connection to
designate a 120-V mid-tap voltage with a 240-V full-winding voltage

## Slide 121
A winding which is appropriate for series, multiple, and three-wire connections will have the designation of multiple voltage rating followed by a slash and the series voltage rating, e.g., the notation 120/240 means that the winding is appropriate either for 120-V multiple connection, for 240-V series connection, and for 240/120 three-wire connection.
To reduce installation costs to a minimum, small distribution transformers are made for pole mounting in overhead distribution. To reduce size and weight, preferred oriented steel is commonly used in their construction.
When two voltages are separated by a cross (x), a winding is indicated which is appropriate for both multiple and series connection but not for three-wire connection. The notation 120 x 240 is used to differentiate a winding that can be used for 120-V multiple connection and for 240-V series connection, but not for a three-wire connection. Examples of all symbols used are given in Table 3-2.
Transformers 100 kVA and below are attached directly to the pole, and transformers larger than 100 up to 500 kVA are hung on crossbeams or support lugs. If three or more transformers larger than 100 kVA are used, they are installed on a platform supported by two poles.
In underground distribution, transformers are installed in Street vaults, in manholes direct-buried, on pads at ground level, or within buildings.
The type of transformer may depend upon soil content, lot location, public acceptance, or cost.

## Slide 123
The distribution transformers and any secondary-service junction devices are installed within elements, usually placed on either the front or the rear lot lines of the customer’s premises. The installation of the equipment to either front or rear locations may be limited by customer preference, local ordinances, and landscape conditions, etc. The rule of thumb requires that a transformer be centrally located with respect to the ]oad it supplies in order to provide proper cable economy, voltage drop, and athetic effect.
Secondary-service junctions for an underground distribution system can be of the pedestal, hand-hole, or direct-buried splice types. No junction is required if the service cables are connected directly from the distribution transformer to the user’s apparatus.
Secondary or service conductors can be either copper or aluminum. However, in general, aluminum conductors are mostly used due to cost savings. The cables are single-conductor or triplexed. Neutrals may be either bare or covered, installed separately, or assembled with the power conductors. All secondary or service conductors are rated 600 V, and their sizes differ from 6 AWG to 1000 kcmil.

## Slide 124
TYPES OF DISTRIBUTION TRANSFORMERS
Heat is a limiting factor in transformer loading.
Removing the coil heat is an important task.
In liquid-filled types, the transformer coils are immersed in a smooth-surfaced, oil-filled tank. Oil absorbs the coil heat and transfers it to the tank surface which, in turn, delivers it to the surrounding air
For transfOrmers 25 kVA and larger, the size of smooth tank surface required to dissipate the heat becomes larger than that required to enclose coils. Therefore the transformer tank may be corrugated to add surface, or external tubes may be welded to the tank. To further increase the heat-disposal capacity, air may be blown ovei the tube surface. Such designs are known as forced-air-cooled, with respect to self-cooled types. Presently, however, all distribution transformers are built to be self-cooled.
Therefore the distribution transformers can be classified as
dry-type and
The dry-type distribution transformers are air-cooled and air-insulated.
(2) liquid-filled-type.
The liquid-filled-type distribution transformers can further be classified as (1) oil-filled and (2) inerteen-filled.

## Slide 125
The distribution transformers employed in overhead distribution systems can be categorized as:
1. Conventional transformers
2. Completely self-protecting (CSP) transformers
3. Completely self-protecting for secondary banking (CSPB) tranformers
The conventional transformers have no integral lightning, fault, or overload protective devices provided as a part of the transformer.
The CSPB distribution transformers are designed for banked secondary service. They are built similar to the CSP transformers, but they are pràvided with two sets of circuit breakers. The second set is used to sectionalize the secondary when it is needed.
The completely sell- protecting (CSP) transformers are, as the name implies, self-protecting from lightning or line surges, overloads, and short circuits. Lightning arresters mounted directly on the transformer tank, as shown in Fig. 3-1, provide the primary winding against the lightning and line surges. The overload protection is provided by circuit breakers inside the transformer tank. The transformer is protected against an internal fault by internal protective links located between the primary winding and the primary bushings. Single-phase CSP transformers (oil-immersed, pole- mounted, 65° C, 60 Hz, 10—500 kVA) are available for a range of primary voltages from 2400 to 34,400 V. The secondary voltages are 120/240 or 240/480/277 V.

## Slide 126
Figure 3-1 Overhead pole-mounted distribution transformers: (a) single. phase CSP (or conventional)

## Slide 127
The distribution transformers employed in underground distribution systems can be categorized as: 1. Subway transformers 2. Low-cost residential transformers 3. Network transformers
Figure 3-2 shows various types of trãnsformes.
Figure 3-2a shows a typical secondary-unit substation with the high voltage and low voltage on opposite ends and full-length flanges for close coupling to high-voltage and low-voltage switch- gear. These units are.normally made in sizes from 75 to 2500 kVA, three-phase, to 35-kY class.
A typical single-phase pole-type transformer for a normal utility application is shown in Fig. 3-2b. These are made from 10 to 500 kVA for delta and wye systems (one-bushing or two-bushing high voltage).
Figure 3-2c shows a typical single-phase pad-mounted (minipad) utility-type transformer.
A typical three-phase pad-mounted (stan-pad) transformer used by utilities as well as industrial and commercial applications is shown in Fig. 3-2d. They are made from 45 to 2500 kVA normally, but have been made to 5000 kVA on special applications. They are also designed for underground service.
Subway transformers are used in underground vaults. They can be conventional-type or current-protected-type. Low-cost residential transformers are similar to those conventional transformers employed in overhead distribution. Network transformers are employed in the secondary networks. They can be either liquid-filled, ventilated dry-type, or sealed dry-type.

## Slide 128
Figure 3-2 Various types of transformers

## Slide 129
Figure 3-3a shows a typical three-phase subsurface-vault-type transformer used in utility applications in vaults below grade where there is no room to place the transformer elsewhere. These units are made for 75 to 2500 kVA and are made of a heavier gauge steel, special heavy corrugated radiators for cooling, and a special coal-tar type of paint.
A typical mobile transformer is shown in Fig. 3-3b. These units are made for emergency applications and to allow utilities to reduce inventory. They are made typically for 500 to 2500 kVA. They can be used on underground service as well as overhead service. Normally they can have two or three primary voltages and two or three secondary voltages, so they may be used on any system the utility may have. For an emergency outage this unit is simply driven to the site, hooked up, and the power to the site is restored.
Figure 3-3c shows a typical power transformer. This class of unit is manufactured from 3700 kVA to 30 MVA up to about 138-kV class. The picture shows removable radiators to allow for a smaller size during shipment, and fans for increased capacity when required, including an automatic on-load tap changer which changes as the voltage varies.
Table 3-3 presents electrical characteristics of typical single-phase distributjon transformers.

## Slide 130
Figure 3-3 Various types of transformers. (Baheau Standard Inc.)

## Slide 131
Table 3-3 Electrical characteristics of typical single-phase distribution transformers*

## Slide 132
REGULATION
To calculate the transformer regulation for a kilovoltampere load of power factor cos ,•at rated voltage, any one of the following formulas can be used:
or
or

## Slide 133
Note that the percent regulation at unity power factor is

## Slide 134
TRANSFORMER EFFICIENCY
The efficiency of a transformer can be calculated from
The total losses include the losses in, the electric circuit, magnetic circuit, and dielectric circuit. Stigant and Franklin [3, p. 97] state that a transformer has its highest efficiency at a load at which the iron loss and copper loss are equal. Therefore the load at which the efficiency is highest can be found from
With the cost of electric energy presently 5 to 6 cents/kWh and projected to double within the next 10 to 15 years, asshown in Fig. 3-6, the cost efficiency of transformers now shifts to align itself with energy efficiency.

## Slide 135
Figure 3—6 Cost of electric energy

## Slide 136
In general, the distribution transformer costs can be classified
the cost of demand lost (i.e., the cost of lost capacity) due to the losses in the transformer.
the cost of lost energy due to the losses in the transformer, and
the cost of investment
Figure 3-7 shows the annual cost per unit load vs. load level.

## Slide 137
TRANSFORMER POLARITY
Transformer-winding terminals are marked to show polarity, to indicate the high- from the low-voltage side. Primary and secondary are not identified as such because which is which depends on input and output connections.
Transformer polarity is an indication of the direction of current flowing through the high-voltage leads with respect to the direction of current flow through the low-voltage leads at any given instant.
In other words, the transformer polarity simply refers to the relative direction of induced voltages between the high-voltage leads and the low-voltage terminals.
The polarity of a single-phase distribution transformer may be additive or subtractive.
Fig. 3-8a, the transformer is said to have subtractive polarity.
On the other hand, when terminals H1 and x1 are diagonally. opposite, as shown in Fig. 38Sb, the transformer is said to have additive polarity.
Transformer polarity can be determined by performing a simple test in which two adjacent terminals of the high- and low-voltage windings are connected together and a moderate voltage is applied to the high-voltage winding, as shown in Fig. 3-9, and then the voltage between the high- and low-voltage winding terminals that are not connected together are measured

## Slide 140
TERMINAL OR LEAD MARKINGS
The terminals or leads of a transformer are the points to which external electric circuits are connected.
According to NEMA and ASA standards, the higher- voltage winding is identified by HV or H, and the lower-voltage winding is identified by LV or x.
Transformers with more than two windings have the windings identified as H, x, y, and z, in order of decreasing voltage. The terminal H1 is located on the right-hand side when facing the high-voltage side of the transformer.
On single-phase transformers the leads are numbered so that when H is connected to x1, the voltage between the highest-numbered H lead and the highest-numbered x lead is less than the voltage of the high-voltage winding.
On three-phase transformers, the terminal H1 is on the right-hand side when facing the high-voltage winding, with the H2 and H3 terminals in numerical sequence from right to left.
The terminal x1 is on the left-hand side when facing the low-voltage winding, with the x2 and x3 terminals in numerical sequence from left to right.

## Slide 141
DISTRIBUTION TRANSFORMER LOADING GUIDES
The rated kilovoltamperes of a given transformer is the output which can be obtained continuously at rated voltage and frequency without exceeding the specified temperature rise.
Based on Appendix C57.91 entitled The Guide for Loading Mineral Oil— Immersed Overhead-Type Distribution Transformers with 55°C and 65°C Average Winding Rise [4], which is an appendix to the ANSI Overhead Distribution Standard C57.12, twenty transformer insulation-life curves were developed.
Temperature rise is used for rating purposes rather than actual temperature, since the ambient temperature may vary considerably under operating conditions.
The life of insulation commonly used in transformers depends upon.the temperature the insulation reaches and the length of time that this temperature is sustained.
Therefore, before the overload capabilities of the transformer can be determined, the ambient temperature, preload conditions, and the duration of peak loads must be known.
These curves indicate a minimum life expectancy of 20 years at 95°C and 110°C hot-spot temperatures, for 55°C and 65°C rise transformers.
Previous transformer loading guides were based on the so-called 8°C insulation-life rule.

## Slide 142
EQUIVALENT CIRCUITS OF A TRANSFORMER
Figure 3-10 shows an equivalent circuit of a single-phase two-winding transformer
Figure 3-11 shows an equivalent circuit of a loaded transformer.
Therefore
or

## Slide 144
As shown in Fig. 3-12, the excitation current Ie also has two components, namely,
the magnetizing- current component Im and
(2) the core-loss component Ic
Figure 3-13 shows an approximate equivalent circuit with combined primary and reflected secondary and load impedances.

## Slide 145
Since the excitation current Ie is very small with respect to I2/n for a loaded transformer, the former may be ignored, as shown in Fig. 3-14.

## Slide 146
Therefore the equivalent impedance of the transformer referred to the primary is
and therefore the equivalent resistance and reactance of the transformer referred to the primary are
As before in Fig. 3-15, for large-size power transformers,

## Slide 147
therefore the equivalent impedance of the transformer becomes as

## Slide 148
SINGLE-PHASE TRANSFORMER CONNECTIONS
Single-phase distribution transformers have one high-voltage primary winding and two low-voltage secondary windings which are rated at a nominal 120 V
Figure 3-16 shows various connection diagrams for single-phase transformers supplying single-phase loads.
Secondary coils each rated at a nominal 120 V may be connected in parallel to supply a twowire 120-V circuit, as shown in Fig. 3-16a and b, or they may be connected in series to supply a three-wire 120/240-V single circuit, as shown in Fig. 3-16c and d.
The connections shown in Fig. 3-16a and b are used where the loads are comparatively small and the length of the secondary circuits is short.
On the other hand, a mistake in polarity when connecting the coils in series (see Fig. 3-16c) will result in the voltage across the outer conductors being zero instead of 240 V. Taps for voltage adjustment, if provided, are located on the high-voltage winding of the transformer.
Figure 3-17 shows single-phase transformer connections for single- and two-bushing transformers to provide customers who require only 240-V single-phase power. These connections are used for small industrial applications.

## Slide 151
Single-phase Transformer Paralleling
The single-phase transformers can be of either additive or subtractive polarity as long as the following conditions are observed and connected, as shown in Fig. 3-18.
1. All transformers have the same turns ratio.
2. All transformers are connected to the same primary phase.
3. All transformers have identical frequency ratings.
4. All transformers have identical voltage ratings.
5. All transformers have identical tap settings.
6. Per unit impedance of one transformer is between 0.925 and 1.075 of the other in order to maximize capability.
However, paralleling two single-phase transformers is not economical since the total cost and losses of two small transformers are much larger than one large transformer with the same capacity.
Therefore, it should be used only as a temporary remedy to provide for increased demands for single-phase power in emergency situations.
Figure 3-19 shows two single-phase transformers, each with two bushings, connected to a two-conductor primary to supply 120/240-V single- phase power on a three-wire secondary.

## Slide 154
To illustrate load division among the parallel-connected transformers, consider the two transformers connected in parallel and feeding a load, as shown in Fig. 3-20.

## Slide 155
Figure 3-21 shows the corresponding equivalent circuit referred to as the low-voltage side.

## Slide 156
Since the transformers are connected in parallel, the voltage drop through each transformer must be equal. Therefore
From which
From Eq. (3-19) it can be seen that the load division is determined only by the relative ohmic impedance of the transformers.
Equation (3-20) can be expressed in terms of kilovoltamperes supplied by each transformer

## Slide 157
Example 3-1 Figure 3-22 shows an equivalent circuit of a single-phase transformer with three-wire secondary for three-wire single-phase distribution.
The typical distribution transformer is rated as 25 kVA, 7200—120/240 V, 60 Hz, and has the following per unit impedance based on the transformer ratings and based on use of the entire low-voltage (LV) winding with zero neutral current:

## Slide 158
Here, the two halves of the low voltage may be independently loaded, and, in general, the three-wire secondary load will not be balanced. Therefore, in general, the equivalent circuit needed is that of a three-winding single-phase transformer as shown in Fig. 3-22, when voltage drops and/or fault currents are to be càmputed. Thus use the meager amount of data (it is all that is usually available) and evaluate numerically all the impedances shown in Fig. 3-22.
SOLUTION Figure 3-22 is based on the reference by Lloyd [1]. To determine 2HX1. approximately, Lloyd gives the following formula:
From Fig. 3-22, the turns ratio of the transformer is
Since the given per unit impedances of the transformer are based on the use of the entire low-voltage winding,

## Slide 159
Also, from Eq. (3-22),
Therefore
and

## Slide 160
APPLICATION OF
DISTRIBUTION
TRANSFORMERS

## Slide 161
THREE-PHASE CONNECTIONS
Common methods of connecting three single-phase transformers for three- phase transformations are the delta-delta (∆- ∆), wye-wye (Y-Y), wye-delta (Y- ∆), and delta-wye (∆ -Y) connections. Here, it is assumed that all transformers in the bank have the same kilovoltampere rating.
The - ∆ Transformer Connection
Figures 3-25 and 3-26 show the delta-delta connection formed by tying together single-phase transformers to provide 240-V service at 0 and 180° angular displacements, respectively.
This connection is often used to supply a small single-phase lighting load and three-phase power load simultaneously.
To provide this type of service the mid-tap of the secondary winding of one of the transformers is grounded and connected to the secondary neutral conductor, as shown in Fig. 3-27.

## Slide 165
Assume that Fig. 3-28 shows the equivalent circuit of a delta-delta-connected transformer bank referred to the low-voltage side. A voltage-drop equation can be written for the low-voltage windings as

## Slide 166
where
Therefore Eq. (3-23) becomes
For the delta-connected secondary
From Eq. (3-25),

## Slide 167
If the three transformers shown in Fig. 3-28 have equal percent impedance and equal ratios of percent reactance to percent resistance, then Eq. (3-30) to (3-32) can be expressed as

## Slide 168
Example 3-5 Three single-phase transformers are connected delta-delta to provide power for a three-phase wye-connected 200-kVA load with a 0.80 lagging power factor and a 80-k VA single-phase light load with a 0.90 lagging power factor, as shown in Fig. 3-29.

## Slide 169
Assume that the three single-phase transformers have equal percent impedance and equal ratios of percent reactance to percent resistance. The primary-side voltage of the bank is 7620/13,200 V and the secondary-side voltage is 240 V. Assume that the single-phase transformer connected bçtween phases b and c is rated at 100 kVA and the other two are rated at 75 kVA. Determine the following: (a) The line current flowing in each secondary-phase wire. (b) The current flowing in the secondary winding of each transformer. (c) The load on each transformer in kilovoltamperes (d) The current flowing in each primary winding of each transformer. (e) The line current flowing in each primary-phase wire.
SOLUTION (a) Using the voltage drop P, as the reference, the three-phase components of the line currents can be found as

## Slide 170
Since the three-phase load has a lagging power factor of 0.80
The single-phase component of the line currents can be found as

## Slide 171
Since the single-phase load has a lagging power factor of 0.90, the current phasor I lags its voltage phasor V by —25.8°. Also, since the voltage phasor V. lags the voltage reference 1’,, by 90° (see Fig. 3-26), then the current phasor ‘bc will lag the voltage reference T°, by — 115.8° (or —25.8° — 90°). Therefore
Hence the line currents owing in each secondary-phase wire can be found as

## Slide 172
The Open- ∆ Open-∆ Transformer Connection
The delta-delta connection is the most flexible of the various connection forms. One of the advantages of this connection is that if one transformer becomes damaged or is removed from service, the remaining two can be operated in what is known as the open-delta or V connection, as shown in Fig. 3-30.

## Slide 173
Assume that a balanced three-phase load with unit power factor is served by all three transformers of a delta-delta bank.
The taking out of one of the transformers from the service will result in having the currents in the other two transformers increase by a ratio of 1.73, even though the output of the transformer bank bank is the same with a unity power factor as before.
However, the individual transformers now function at a power factor of 0.866. One of the transformers delivers a leading load and the other a lagging load.
To operate the remaining portion of the delta-delta transformer bank (i.e., the open-delta open-delta bank) safely, the connected load has to be decreased by the 57.7 percent which can be found as follows:
and

## Slide 174
Figure 3-31 shows an open-delta connection for 240-V three-phase three-wire secondary service at 00 angular displacement. The neutral point n shown in the low-voltage phasor diagram exists only on the paper.

## Slide 175
For the sake of illustration, assume that a balanced three-phase load, e.g., an induction motor as shown in the figure, with a lagging power factor is connected to the secondary. Therefore the a, b, c phase Currents in the secondary can be found as
The transformer kilovoltampere loads can be calculated as follows. The kilovoltampere load on the first transformer is

## Slide 176
and the kilovoltampere load on the second transformer is
Therefore, the total load that the transformer bank can be loaded to (or the total “effective” transformer bank capacity) is
and hence,

## Slide 177
For example, if there are two 50-kVA transformers in the open-delta bank, even though the total transformer bank capacity appears to be
in reality the. bank’s “effective” maximum capacity is
On the other hand, if there are three 50-kVA transformers in the delta-delta bank, the bank’s maximum capacity is
which shows an increase of 73 percent over the 86.6-kVA load capacity. Assume that the load power factor js cos U and its angle can be calculated as

## Slide 178
or using, Van as the reference,
If θIn, is negative, then θ is positive which means it is the angle of a lagging load power factor. Also, it can be shown that

## Slide 179
On the other hand, the transformer power factors for transformers 1 and 2 can be calculated as

## Slide 180
and, similarly, the total reactive power output of the bank is
Table 3-6 The effects of the load power factor on the transformer power factors

## Slide 181
The Y-Y Transformer Connection
Figure 3-32 shows three transformers connected wye-wye on a typical three- phase four-wire multigrounded system to provide for 120/208Y-V service at 00 angular displacement.

## Slide 182
The Y-∆ Transformer Connection
Figure 3-33 shows three single-phase transformers connected in wye-delta on a three-phase three-wire undergrounded-wye, primary system to provide for 120/208/240-V three-phase four-wire delta secondary service at 300 angular disp1acement.

## Slide 183
Figure 3-34 shows three transformers connected in wye-delta on a typical three-phase four-wire grounded-wye primary system to provide for 240-V three- phase three-wire delta secondary service at 210° angular displacement.

## Slide 184
The wye-delta connection is advantageous in many cases because the voltage between the outside legs of the wye is 1.73 times the voltage to neutral, so that higher distribution voltage can be gained by using transformers with primary winding of only the voltage between any leg and the neutral. For example, 2.4-kV primary single-phase transformers can be connected in wye on the primary to a 4.1 6-ky three-phase wye circuit.
In the wye.delta connection the voltage/transformation ratio of the bank is 1.73 times the voltage/transformation ratio of the individual transformers. When transformers of different capacities are used, the maximum safe bank rating is three times the capacity of the smallest transformers.
The approximate rated capacity required in a wyedelta-connected bank with an isolated bank neutral to serve a combined three- phase and single-phase load, assuming unity power factor, can be found as
which is equal to rated transformer capacity across lighting phase,

## Slide 185
The Open Wyei – Open ∆ Transformer Connection
As shown in Fig. 3-35, in the case of having one phase of the primary supply opened, the transformer bank becomes open-wye open-delta and continues to serve the three-phase load at a reduced capacity.

## Slide 186
Example 3-6 Two single-phase transformers are connected open-wye open- delta to provide power for a three-phase wye-connected 100-kVA load with a 0.80 lagging power factor and a 50-kVA single-phase load with a 0.90 lagging power factor, as shown in Fig. 3-36.

## Slide 187
Assume that the primary-side voltage of the bank is 7620/13,200 V and the secondary-side voltage is 240 V. Using the given information, calculate the following: (a) The line current flowing in each secondary-phase wire. (b) The current flowing in the secondary winding of each transformer. (c) The kilovoltampere load on each transformer. (d) The current flowing in each primary-phase wire and in the primary neutral.
SOLUTION (a) Using the voltage drop Va,, as the reference, the three-phase components of the line currents can be found as

## Slide 188
The ∆-Y Transformer Connection

## Slide 190
The additional conditions to successfully parallel three-phase distribution transformers are the following:
1. All transformers have identical frequency ratings. 2. All transformers have identical voltage ratings. 3. All transformers have identical tap settings. 4. Per unit impedance of one transformers between 0.925 and 1.075 of the other.
However, if two of the units have the identical impedance values and the third unit has an impedance value which is within, plus or minus, 25 percent of the ininedance value of the like transformers, it is possible to operate the delta-delta bank, with a small unbalanced transformer loading, at reduced bank output capacity. Table 3-5 gives the permissible amounts of load unbalanced on the odd and like transformers.

## Slide 191
The delta-wye step-up and wye-delta step-down connections are especially suitable for high-voltage transmission systems. They are economical in cost, and they supply a stable neutral point to be solidly grounded or grounded through resistance of such value as to damp the system critically and prevent the possibility of oscillation.

## Slide 192
THREE-PHASE TRANSFORMERS
Three-phase voltages may be transformed by means of three-phase transformers. The core of a three-phase transfOrmer is made with three legs, a primary and secondary winding of one phase being placed on each leg.
It is possible to construct the core with only three legs since the fluxes established by the three windings are 1200 apart in time phase.
Two core legs act as the return for the flux in the third leg. For example, if flux is at a maximum value in one leg at some instant, the flux is half that value and in the opposite direction through the other two legs at the same instant.
The three-phase transformer takes less space than do three single-phase transformers having the same total capacity rating since the three windings can be placed together on one core.
Three-phase transformers can be connected in any of the aforementioned connection types. The difference is that all connections are made inside the tank.

## Slide 193
Figure 3-39 shows a delta-delta connection for 120/2081240-V three-phase four-wire secondary service at 0° angular displacement.

## Slide 194
Figure 3-40 shows a three-phase open-delta connection for 120/240-V Service. It is used to supply large 120- and 240-V single-phase loads simultaneously with small amounts of three-phase load. The two sets of windings in the transformer are of different capacity sizes in terms of kilovoltamperes

## Slide 195
Figure 3-41 shows a three-phase wye-delta connection for 120/240-V service at 30° angular displacement. It is used to supply three-phase 240-V loads and small amounts of 120-V single-phase loads.

## Slide 196
Figure 3-42 shows a three-phase open-wye open-delta connection for 120/240-V service at 30° angular displacement. The statements on efficiency and capacity for three-phase open-delta connection are also applicable for this connection.

## Slide 197
Figure 3-43 shows a three-phase transformer connected in wye-wye for 120/208Y-V service. The connection allows single-phase loads to balance

## Slide 198
THE T OR SCOTT CONNECTION
In some localities, two-phase is required from a three-phase system.
The T or Scott connection, which employs two transformers, is the most frequently used connection for three-phase to two-phase (or even three-phase) transformations.
In general, the T connection is primarily used for getting a three-phase transformation, whereas the Scott connection is mainly used for getting a two-phase transformation. In either connection type, he basic design is the same.
FIgure 3-44 The T or Scott connection for three-phase to two-phase three-wire, transformer.

## Slide 199
The first transformer is called the main transformer and connected from line to line, and the second one is called the teaser transformer and connected from the midpoint of the first transformer to the third line. It dictates that the midpoints of both primary and secondary windings be available for connections. The secondary may be either three-, four-, or five-wire, as shown in the figures.
Figure 3-45 The T or Scott connection for three-phase to two-phase, four-wire, transformation.

## Slide 200
Figure 3-46 The T or Scott connection for three-phase to two-phase, five-wire, transformation.
The T or Scott connections change the number of phases but not the power factor, which means that a balanced load on the secondary will result in a balanced load on the primary.
When the two-phase load at the secondary has a unity power factor, the main transformer operates at 86.6 percent power factor and the teaser transformer operates at unity power factor. These connections can transform power in either direction, i.e., from three-phase to two-phase or from two-phase to three-phase.

## Slide 201
Example 3-7 Two transformer banks are sometimes used in distribution systems, as shown in Fig. 3-47, especially to supply customers having large single-phase lighting loads and small three-phase (motor) loads.

## Slide 202
The low-voltage connections are three-phase four-wire 120/240 V open- delta. The high-voltage connections are either open-delta or open-wye. If it is open-delta, the transformer-rated high voltage is the primary line-to-line voltage. If it is open-wye, the transformer-rated high voltage is the primary line-to-neutral voltage.
Assume that ABC phase sequence is used in the connections for both high voltage and low voltage and the phasor diagrams and
and
Also assume that the left-hand transformer is used for lighting. To. establish the two-transformer bank with open-delta primary and open-delta secondary: (a) Draw and/or label the voltage phasor diagram required for the open-delta primary and open-delta secondary on the 0° references given. (b) Show the connections required for the open-delta primary and open- delta secondary.
SOLUTION
Figure 3-48 illustrates the solution.

## Slide 203
Note that, because of Kirchhofl’s voltage law, there are V4 and V voltages between A and C and between a and c, respectively. Also note that the midpoint of the left-hand transformer is grounded to provide the 120 V for lighting loads.

## Slide 204
THE AUTOTRANSFORMER
The usual transformer has two windings (not including a tertiary, if there is any) which are not connected to each other, whereas an autotransformer is a transformer in which one winding is connected in series with the other as a single winding.
In this sense, an aütotransformer is a normal transformer connected in a special way. It is rated on the basis of output kilovoltamperes rathet than the transformer’s kilovoltamperes.
It has lower leakage reactance, lower losses, smaller excitation current requirements, and, most of all, it is cheaper than the equivalent two-winding transformer (especially when the voltage ratio is 2:1 or less).
Figure 3-54 shows the wiring diagram of a single-phase autotransformer. Note that S and C denote the series and common portions of the winding.

## Slide 205
There are two voltage ratios, namely, circuit and winding ratios. The circuil ratio is
As can be observed from Eq. (3-67), the circuit ratio is always larger than I. On the other hand, the winding-voltage ratio is
Of course, the current ratio is

## Slide 206
Therefore the circuits voltampere rating for an ideal autotransformer is
and the windings voltampere rating is
Therefore the capacity of an autotransformer can be compared tothe capacity of an equivalent two-winding transformer (assuming the same core and coils are used) as

## Slide 207
For example, if n is given as 2, the ratio, given by Eq. (3-72), is 2, which means that Capacity as autotransformer = 2 x capacity as two-winding transformer.
Therefore one can use a 500-k VA autotransformer instead of using a 1000-k VA two-winding transformer. Note that as n approaches 1, which means that the voltage ratios approach 1, such as 7.2 kV/6.9 kV, then the savings, in terms of the core and coil sizes of autotransformer, increases.
An interesting case happens when the voltage ratio (or the turns ratio) is unity: the maximum savings is achieved but then there is no need for any transformer since the high and low voltages are the same.
Figure 3-55 shows a single-phase autotransformer connection used in distribution systems to supply 120/240-V single-phase power from an existing 208Y/120-V three-phase system, the most economically.

## Slide 209
Figure 3-56 shows a three-phase autotransformer wye-wye connection used in distribution systems to increase voltage at the ends of feeders or where extensions are being made to existing feeders.

## Slide 210
THE BOOSTER TRANSFORMERS
Booster transformers are also called the buck-and-boost transformers and provide a fixed buck or boost voltage to the primary of a distribution system when the line voltage drop is excessive. The transformer connection is made in such a way that the secondary is in series and in phase with the main line.
The connections shown in Fig. 3-57a and b boost the voltage 5 and 10 percent, respectively. In Figure 3-57a, if the lines to the low-voltage bushings x3 and x1 are interchanged, a 5 percent buck in the voltage results.

## Slide 211
Figure 3-58 shows a three-phase three-wire booster transformer connection using two single-phase booster transformers.

## Slide 212
Figure 3-59 shows a three-phase four-wire booster transformer connection using three single-phase booster transformers.

## Slide 213
PROBLEMS
REFERENCES
Westinghouse Electric Corporation: Electric Utility E.ngineerfng Reference Book—Distribution Systems, vol. 3 East Pittsburgh, Pa., 1965
Westinghouse Electric Corporation: Electrical Transmission and Distribution Reference Book, East Pittsburgh, Pa., 1964.
Stigant, S. A., and A. C. Franklin: The .T&P Transformer Book, Butterworth, London, 1973
The Guide for Loading Mineral Oil—Immersed Overhead-Type Distribution Transformers with 55°C and 65°C Average Winding Rise, American National Standards Institute, Appendix C57.91-1969
Fink, D. G., and H. W. Beaty: Standard Handbook for Electrical Engineers, 11th ed., McGraw-Hill, New York, 1978
Clarke, E.: Circuit Analysis of AC Power Systems, vol. 1, General Electric Series, Schenectady, N.Y., 1943.
General Electric Company: Distribution Transformer Manual, Hickory, NC., 1975.

## Slide 214
DESIGN OF SUBTRANSMISSION LINES AND
DISTRIBUTION SUBSTATIONS

## Slide 215
INTRODUCTION
In a broad definition, the distribution system is that part of the electric utility system between the bulk power source and the customers’ service switches.
This definition of the distribution system includes the following components:
I. Subtransmission system 2. Distribution substations 3. Distribution or primary feeders 4. Distribution transformers 5. Secondary circuits 6. Service drops

## Slide 216
I. Subtransmission system
2. Distribution substations
3. Distribution or primary feeders
5. Secondary circuits
6. Service drops
4. Distribution transformers

## Slide 217
SUBTRANSMISSION
The subtransmission system designs vary from simple radial system to a subtransmission network. The major considerations affecting the design are cost and reliability.

## Slide 218
Figure 4-3 Improved form of radial-type subtrarismission.

## Slide 219
FIgure 4-4 Loop-type subtransmission.

## Slide 220
Figure 4-5 Grid- or network-type subtransniission.

## Slide 221
DISTRIBUTION SUBSTATIONS
Distribution substation design has been somewhat standardized by the electric utility industry based upon past experiences. However, the process of standardiztiori is a continuous one.

## Slide 222
Figure 4-7 A typical small distribution substation. (S&C Eleciric Company.)

## Slide 223
Figure 4-8 Overview of a modern substatioan ( S&C Electric company)

## Slide 224
Figure 4-9 Close view of a typical modem distribution substation transformer.(Westinghouse Electric Company.)
A typical substation may include the following equipment:
(1) power transformers,
(2) circuit breakers,
(3) disconnecting switches,
(4) station buses and insulators,
(5) current-limiting reactors,
(6) shunt reactors,
(7) current transformers,
(8) potential transformers,
(9) capacitor voltage transformers,
(10) coupling capacitors,
(11) series capacitors,
(12) shunt capacitors,
(13) grounding system,
(14) lightning arresters and/or gaps,
(15) line traps,
(16) protective relays,
(12) shunt capacitors,
(18) other apparatus.
(17) station batteries, and
(18) other apparatus.

## Slide 225
SUBSTATION BUS SCHEMES
The electrical and physical arrangements of the switching and busing at the sub- transmission voltage level are determined by the selected substation scheme (or diagram). On the other hand, the selection of a particular substation scheme is based upon safety, reliability, economy, simplicity, and other considerations.
The most commonly used substation bus schemes include
(1) single bus scheme;
(2) double bus—double breaker (or double main) scheme;
(3) main-and- transfer bus scheme;
(4) double bus—single breaker scheme;
(5) ring bus scheme; and
(6) breaker-and-a-half scheme.

## Slide 227
Fig. 4-11 gives a typical double bus—double breaker scheme;

## Slide 228
Fig. 4-12 illustrates a typical main-and-transfer bus scheme;

## Slide 229
Fig. 4-13 shows a typical double bus—single breaker scheme;

## Slide 230
Fig. 4-14 gives a typical ring bus scheme;

## Slide 231
Fig 4-15 illustrates a typical breaker-and-a-half scheme.

## Slide 236
SUBSTATION LOCATION
The location of a substation is dictated by the voltage levels, voltage regulation considerations, subtransmissiôn costs, substation costs, and the costs of primary feeders, mains, and distribution transformers.
It is also restricted by other factors, as explained in Chap. 1, which may not be technical in nature.
However, to select an ideal location for a substation, the following rules should be observed [2]:
1. Locate the substation as much as fcasible close to the load center of its service area, so that the addition of load times distance from the substation is a minimum.
2. Locate the substiion such that proper voltage regulation can be obtainable without taking extensive measures.
3. Select the substation location such that it provides proper access for incoming subtransmission lines and outgoing primary feeders and also allows for future growth.
4. The selected substation location should provide enough space for the future substation expansion.
5. The selected substation location should not be opposed by land use regulations, local ordinances, and neighbors.
6. The selected substation location should help to minimize the number of customers affected by any service discontinsity. 7. Other considerations, subh’ as adaptability, emergency, etc.

## Slide 237
THE RATING OF A DISTRIBUTION SUBSTATION
The additional capacity requirements of a system with increasing load density can be met by: 1. Either holding the service area of a given substation constant and increasing its capacity 2. Or developing new substations and thereby holding the rating of the given substation constant
It is helpful to assume that ‘the system changes
(1) at constant load density for short-term distribution planning and
(2) at increasing load density for long- term planning.
Further, it is also customary and helpful to employ geometric figures to represent substation service areas, as suggested by Van Wormer [3], Denion and Reps [4], and Reps It simplifies greatly the comparison of alternative plans which may require different sizes of distribution substation, different numbers of primary feeders, and different primary-feeder voltages.
Reps [5] analyzed a square-shaped service area representing a part of, or the entire service area of, a distribution substation. It is assumed that the square area is served by four primary feeders from a central feed point, as shown in Fig. 4-16.

## Slide 239
Here, the percent voltage drop from the feed point a to the end of the last lateral at c is
Reps [5] simplified the above voltage-drop calculation by introducing a constant K which can be defined as percent voltage drop per kilovoltampere-mile.
Figure 4-17 is developed for three-phase overhead lines with an equivalent spacing of 37 in between phase conductors.
The following analysis is based on the work done by Denton and Reps [4] and Reps [5]. In Fig. 4-16, each feeder serves a total load of

## Slide 240
Figure 4-17 The K constant for copper conductors, assuming a lagging-load power factor of 0.9.

## Slide 241
Equation (4-1) can be rewritten as
since
where I4 is the linear dimension of the primary-feeder service area in miles.
Assuming uniformly distributed load, i.e., equally loaded and spaced distribution transformers, the voltage drop in the primary-feeder main is
or substituting Eq. (4-2) into Eq. (4-4),
In Eq. (4-4) and (4-5), it is assumed that the total or lumped-sum load is located at a point on the main feeder at a distance of x 14 from the feed point a.

## Slide 242
Reps [5] extends the discussion to a hexagonally shaped service area supplied by six feeders from the feed point which is located at the center, as shown in Fig. 4-18.

## Slide 243
Assume that each feeder service area is equal to one-sixth of the hexagonally shaped total area, or
Here, each feeder serves a total load of
or substituting Eq. (4-6) into Eq. (4-7),

## Slide 244
As before, it is assumed that the total or lump-sum is located at a point on the main feeder at a distance of x 16 from the feed point. Therefore, the percent voltage drop in the main feeder is
or substituting Eq. (4-8) into Eq. (4-9),

## Slide 245
GENERAL CASE: SUBSTATION SERVICE AREA WITH n PRIMARY FEEDERS
Denton and Reps [4] and Reps [5] extend the discussion to the general case in which the distribution substation service area is served by n primary feeders emanating from the point, as shown in Fig. 4-19.

## Slide 246
Assume that the load in the service area is uniformly distributed and each feeder serves an area of triangular shape. The differential load served by the feeder in a differential area of dA is
where dS = differential load served by the feeder in the differential area of dA, kVA
D = load density, kVA/mi2 dA = differential service area of the feeder, mi2
or
In Fig. 4-19, the following relationship exists:

## Slide 247
Therefore the total service area of the feeder can be calculated as
Hence, the total kilovoltampere load served by one of n feeders can be calculated as
This total load is located, as a lump-sum load, at a point on the main feeder at a distance of 2/3 x I4 from the feed point a.
Therefore, the summation of the percent voltage contributions of all such areas is

## Slide 248
or, substituting Eq. (4-15) into Eq. (4-16),
or, since
Eq. (4- 17) can also be expressed as
Equations (4-18) and (4-19) are only applicable when n 3. Table 4-2 gives the results of the application of Eq. (4-17) to square and hexagonal areas. For n = 1 the percent voltage drop in the feeder main is

## Slide 249
Table 4-2 Application results of Eq. (4-17)
and for n = 2 it is
To compute the percent voltage drop in uniformly loaded lateral, lump and locate its total load at a point halfway along its length, and multiply the kilovoltampere-mile product for that line length and loading by the appropriate K constant [5].

## Slide 250
COMPARISON OF THE FOUR- AND SIX-FEEDER PATTERNS
For a square-shaped distribution substation area served by four primary feeders, that is, n = 4, the area served by one of the four feeders is
The total area served by all four feeders is
The kilovoltampere load served by one of the feeders is
Thus the total kilovoltampere load served by all four feeders is

## Slide 251
The percent voltage drop in the main feeder is
The load current in the main feeder at the feed point a is
or
Of course, the ampacity, i.e., the current-carrying capacity, of a conductor selected for the main feeder should be larger than the current values that can be obtained from Eq. (4-27) and (4-28).

## Slide 252
On the other hand, for a hexagonally shaped distribution substation area served by six primary feeders, that is, n = 6, the area served by one of the six feeders is
The total area served by all six feeders is
The kilovoltampere load served by one of the feeders is
Therefore the total kilovoltampere load served by all six feeders is

## Slide 253
The percent voltage drop in the main feeder is
The load current in the main feeder at the feed point a is
or
The relationship between the service areas of the four- and six-feeder patterns can be found under two assumptions: (1) feeder circuits are thermally limited and (2) feeder circuits are voltage-drop-limited.

## Slide 254
1. Thermally limited feeder circuits. For a given conductor size and neglecting voltage drop,
Substituting Eq. (4-28) and (4-35) into Eq. (4-36),
from Eq. (4-37),
Also, by dividing Eq. (4-30) by Eq. (4-23),

## Slide 255
Substituting Eq. (4-38) into Eq. (4-39),
or
Therefore the six feeders can carry 1.50 times as much load as the four feeders if they are thermally loaded.
Substituting Eq. (4-26) and (4-33) into Eq. (4-42) and simplifying the result,
2. Voltage-drop-limited feeder Circuits. For a given conductor size and assuming equal percent voltage drop,

## Slide 256
From Eq. (4-30), the total area served by all six feeders is
Substituting Eq. (4-43) into Eq. (4-23), the total area served by all four feeders is
Dividing Eq. (4-44) by Eq. (4-45),
or
Therefore the six feeders can carry only 1.25 times as much load as the four feeders if they are voltage-drop-limited.

## Slide 257
DERIVATION OF THE K CONSTANT
Consider the primary-feeder main shown in Fig. 4-20.
Here, the effective impedance Z of the three-phase main depends upon the nature of the load. For example, when a lumped-sum load is connected at the end of the main, as shown in the figure, the effective impedance is
where z = impedance of three-phase main line,Ω/(mi . phase) l = length of the feeder main, mi

## Slide 258
When the load is uniformly distributed, the effective impedance is
When the load has an increasing load density, the effective impedance is
Taking the receiving-end voltage as the reference phasor,
from the phasor diagram given in Fig. 4-21,

## Slide 259
the sending-end voltage is
The current is
and the power-factor angle is
and the power factor is a lagging 1. When the real power P and the reactive power Q flow in opposite directions, the power factor is a leading 1.
Here, the per unit voltage regulation is defined as

## Slide 260
and the percent voltage regulation is
or
whereas the per unit voltage drop is defined as
and the percent voltage drop is
or

## Slide 261
From Fig. 4-20 and 4-21, the sending-end voltage is
or
The quantities in Eq. (4-61) can be either all in per units or in the mks (or SI) system. Use line-to-neutral voltages for single-phase three-wire or three-phase three- or four-wire systems.

## Slide 262
In typical distribution circuits,
and the voltage angle 5 is closer to zero or typically
whereas in typical transmission circuits,
since X is much larger than R. Therefore, for a typical distribution circuit, the sin S can be neglected in Eq. (4-6 1). Hence
and Eq. (4-6 1) becomes

## Slide 263
Therefore the per unit voltage drop, for a lagging power factor, is
and it is a positive quantity. The VD is negative when there is a leading j,ower factor due to shunt capacitors or when there is a negative reactance X due to series capacitors installed in the circuits. The complex power at thereceiving end is
Therefore
since

## Slide 264
Substituting Eq. (4-65) into Eq. (4-61), which is the exact equation since the voltage angle ö is not neglected, the sending-end voltage can be written as
or approximately,
Substituting Eq. (4-67) into Eq. (4-5’7),
or
or

## Slide 265
since
and
Equations (4-69) and (4-70) can also be derived from Eq. (7-63), since
The quantities in Eqs. (4-68) and (4-70) can be either all in per units or in the SI system. Use the line-to-neutral voltage values and per phase values for the Pr, Qr, and Sr.
To determine the K constant, use Eq. (4-68)

## Slide 266
or
or
or
where

## Slide 267
Therefore
and it has the unit of
To get the percent voltage drop, multiply the right side of Eq. (4-77) by 100, so that
which has the unit of

## Slide 268
In Eqs. (4-74) to (4-76), s is the effective length of the feeder main which depends upon the nature of the load. For example, when the load is connected at the end of the main as lumped-sum, the effective feeder length is
when the load is uniformly distributed along the main
when the load has an increasing load density,
Example 4-1 Assume that a three-phase 4.16-kV wye-grounded feeder main has 4 copper conductors with an equivalent spacing of 37 in between phase conductors and a lagging-load power factor of 0.9. (a) Determine the K constant of the main by employing Eq. (4-77). (b) Determine the K constant of the main by using the precalculated percent voltage drop per kilovoltampere-mile curves and compare it with the one found in part a.

## Slide 269
(a) From Eq. (4-77),
SOLUTION
Therefore the per unit voltage drop per kilovoltampere-mile is

## Slide 270
or
(b) From Fig. 4-17, the K constant for 4 copper conductors is
which is the same as the one found in part a.
Example 4-2 Assume that the feeder shown in Fig. 4-22 has the same characteristicS as the one in Example 4-1 and a lumped-sum load of 500 kVA with a lagging-load power factor of 0.9 is connected at the end of a 1-mi-long feeder main. Calculate the percent voltage drop in the main.

## Slide 271
SOLUTION
The percent voltage drop in the main is
Example 4-3 Assume that the feeder shown in Fig. 4-23 has the same characteristics as the one in Example 4-2, but the 500-k VA load is uniformly distributed along the feeder main. Calculate the percent voltage drop in the main.

## Slide 272
SOLUTION
where the effective feeder length s is
The percent voltage drop in the main is
Therefore
Therefore, it can be seen that the negative effect of the lumped-sum load on the 7 VD is worse than the one for the uniformly distributed load. Figure 4-23 also shows the conversion of the uniformly distributed load to a lumped- sum load located at point a for the voltage-drop calculation.

## Slide 273
Reps [5] derived the following formula to relate the application of distribution substations to load areas:
Reps [5] and Denton and Reps [4] developed an alternative form of Eq. (4-85) as
SUBSTATION APPLICATION CURVES

## Slide 274
Based on Eq. (4-86), they have developed the distribution substation application curves, as shown in Fig. 4-25 and 4-26.

## Slide 275
The distribution substation application curves are based on the following assumptions [5]: 1. #4/0 AWG copper conductors are used for the. three-phase primary-feeder mains. 2. #4 AWG copper conductors are used for the three-phase primary-feeder laterals. 3. The equivalent spacing between phase conductors is 37 in. 4. A lagging-load power factor of 0.9.
The curves are the plots of number of primary feeders n vs. load density D for numerous values of TSn,,, that is, total kilovoltampere loading of all n primary feeders including a pattern serving the load area of a substation or feed point.
In Fig. 4-25 and 4-26, the curves for n vs. D are given for both constant TSn,, or constant TAn,,, that is, total area served by all n feeders emanating from the feed point or substation.

## Slide 276
INTERPRETATION OF THE PERCENT-VOLTAGE-DROP FORMULA
Equation (4-85) can be rewritten in alternative forms to illustrate the interrelationship of several parameters guiding the application of distribution substations to load areas:

## Slide 277
To illustrate the use and interpretation of the equation, assume five different cases, as shown in Table 4-5.
Case 1 represents an increasing service area as a result of geographic extensions of a city. If the length of the primary feeder is doubled (shown in the table by x 2), holding everything else constant, the service area A of the feeder increases four times, which in turn increases TS and S,, four times, causing the % VD in the feeder to increase eight times. Therefore increasing the feeder length should be avoided as a remedy due to the severe penalty.
Case 2 represents load growth due to load density growth. For example, if the load density is doubled, it causes TS and S,, to be doubled, which in turn increases the % VD1 in the feeder to be doubled. Therefore increasing load density also has a negative effect on the voltage drop.

## Slide 278
Case 3 represents the addition of new feeders. For example, if the number of the feeders is doubled, it causes S to be reduced by half, which in turn causes the % VD to be reduced by half. Therefore, new feeder additions help to reduce the voltage drop.
Case 4 represents feeder reconductoring. For example, if the conductor size is doubled, it reduces the K constant by half, which in turn reduces the y0 VD by half.
Case 5 represents the delta-to-grounded-wye conversion. It increases the line-to-line base kilovoltage by ,J, which in turn decreases the K constant, causing the % VD to decrease to one-third its previous value.

## Slide 279
Example 4-7 To illustrate distribution substation sizing and spacing, assume a square-shaped distribution substation service area as shown in Fig. 4-16. Assume that the substation is served by four three-phase four-wire 2.4/4.16-ky grounded-wye primary feeders. The feeder mains are made of either 2 AWO copper or 1/0 ACSR conductors. The three-phase open-wire overhead lines have a geometric mean spacing of 37 in between phase conductors. Assume a lagging-load power factor of 0.9 and a 1000 kVA/mi2 uniformly distributed load density. Calculate the following: (a) Consider thermally loaded feeder mains and find: (i) Maximum load per feeder (ii) Substation size (iii) Substation spacing, both ways (iv) Total percent voltage drop from the feed point to the end of the main (b) Consider voltage-drop-limited feeders which have 3 percent vàltagc drop and find: (i) Substation spacing, both ways (ii) Maximum load per feeder (iii) Substation size (iv) Ampere loading of the main in per unit of conductor ampacity

## Slide 280
From Tables A-1 and A-5 of Appendix A, the conductor ampacities for 2 AWG copper and fl/0 ACSR conductors can be found as 230 A.
(a) Thermally loaded mains: (i) Maximum load per feeder is
(ii) Substation size is
(iii) Substation spacing, both ways, can be found from
SOLUTION

## Slide 281
Or
Therefore

## Slide 286
DESIGN CONSIDERATIONS
OF PRIMARY SYSTEMS

## Slide 287
INTRODUCTION
The part of the electric utility system which is between the distribution substation and the distribution transformers is called the primary system.
It is made of circuits known as primary feeders or primary distribution feeders.
There are various and yet interrelated factors affecting the selection of a primary-feeder rating.
1. The nature of the load connected
2. The load density of the area served
3. The growth rate of the load
4. The need for providing spare capacity for emergenày operations
5. The type and cost of circuit ãonstruction employed 6. The design and capacity of the substation involved
7. The type of regulating equipment used 8. The quality of service required 9. The continuity of service required

## Slide 289
RADIAL-TYPE PRIMARY FEEDER

## Slide 290
A modified radial-type primary feeder with tie and sectionalizing switches to provide fast restoration of service to customers

## Slide 291
another type of radial primary feeder with express feeder and backfeed

## Slide 292
A radial-type phase-area feeder arrangement in which each phase of the three-phase feeder serves its own service area

## Slide 293
LOOP-TYPE PRIMARY FEEDER

## Slide 294
PRIMARY NETWORK

## Slide 295
PRIMARY-FEEDER VOLTAGE LEVELS
The primary-feeder voltage level is the most important factor affecting the system design, cost, and operation.
Some of the design and operation aspects affected by the primary-feeder voltage level are [2]:
1. Primary-feeder length 2. Primary-feeder loading 3. Number of distribution substations 4. Rating of distribution substations 5. Number of subtransmission lines
6. Number of customers affected by a specific outage 7 System maintenance practices 8. The extent of tree trimming
9. Joint use of utility poles 10. Type of pole-line design and construction
11. Appearance of the pole line

## Slide 296
Factors affecting primary-feeder voltage-level selection decision

## Slide 297
Typical primary voltage levels

## Slide 298
Usually, primary feeders located in low-load density areas are restricted in length and loading by permissible voltage drop rather than by thermal restrictions, whereas primary feeders located in high-load density areas, e.g., industrial and commercial areas, may be restricted by the thermal limitations.
In general, for a given percent voltage drop, the feeder length and loading are direct functions of the feeder voltage level. This relationship is known as the voltage-square rule.
Lokay [2] explains it clearly, the feeder with the increased length feeds more load. Therefore the advantage obtained by the new and higher-voltage level th.rough the voltage-square factor, i.e.,
Further, the same percent voltage drop will always result provided that the following relationship exists:

## Slide 299
The relationship between the voltage-square factor rule and the feeder distancecoverage principle is further explained in Fig. 5-9

## Slide 300
There is a relationship between the area served by a substation and the voltage-rule. Lokay [2] defines it as the area-coverage principle. As illustrated in Fig. 5-10,

## Slide 301
For a constant percent voltage drop and a uniformly distributed load, the feeder service area is proportional to
For example, if the new feeder voltage level is increased to twice the previous voltage level, the new load and area that can be served with the same percent voltage drop is
If the new feeder voltage level is increased to three times the previous voltage level, the new load and area that can be served with the same percent voltage drop is

## Slide 302
PRIMARY-FEEDER LOADING
Some of the factors affecting the design loading of a feeder are:
1. The density of the feeder load
2. The nature of the feeder load
3. The growth rate of the feeder load
4. The reserve-capacity requirements for emergency
5. The service-continuity requirements
6. The service-reliability requirements
7. The quality of service
8. The primary-feeder voltage level
9. The type and cost of àonstruction
10. The location and capacity of the distribution substation
11. The voltage regulation requirements

## Slide 306
TIE LINES
A tie line is a line that connects two supply systems to provide emergency service to one system from another, as shown in Fig. 5-14.

## Slide 307
Therefore tie lines are needed to perform either of the following two functions:
To provide emergency service for an adjacent feeder for the reduction of outage time to the customers during emergency conditions.
To provide emergency service for adjacent substation systems, thereby eliminating the necessity of having an emergency backup supply at every substation. Tie lines should be installed when more than one substation is required to serve the area load at one primary distribution voltage.
DISTRIBUTION FEEDER EXIT: RECTANGULAR-TYPE DEVELOPMENT
the rectangular-type detelopment

## Slide 309
In general, adjacent service areas are served from different transformer banks in order to provide for transfer to adjacent circuits in the event of transformer outages. The addition of new feeder circuits and transformer banks requires circuit number changes as the service area develops.

## Slide 310
RADIAL-TYPE DEVELOPMENT

## Slide 311
RADIAL FEEDERS WITH UNIFORMLY DISTRIBUTED LOAD

## Slide 313
Therefore, from Eq. (5-28), the distance x from the beginning of the main feeder at which location the total load current I may be concentrated, i.e., lumped for the purpose of calculating the total voltage drop, is
the distance x from the beginning of the main feeder at which location the total load current I may be lumped for the purpose of calculating the total power loss is

## Slide 314
RADIAL FEEDERS WITH NONUNIFORMLY DISTRIBUTED LOAD

## Slide 315
APPLICATION OF THE A, B, C, D GENERAL CIRCUIT CONSTANTS
TO RADIAL FEEDERS

## Slide 321
THE DESIGN OF RADIAL PRIMARY DISTRIBUTION SYSTEMS
The radial primary distribution systems are designed in several different ways:
overhead primaries with overhead laterals or
(2) underground residential distribution (URD)
Overhead Primaries
Underground Residential Distribution
The lack of outages caused by the abnormal weather conditions such as ice, sleet, snow, severe rain and storms, and lightning
The lack of outages caused by accidents, fires, and foreign objects
The lack of tree trimming and other preventative maintenance tasks
The aesthetic improvement

## Slide 324
Apparatus, suggested by Lokay [2], that is or has been used to accomplish the desired switching or sectionalizing.

## Slide 325
A distribution trans forme with internal high-voltage fuse and load-break connectors
A distribution transformer with internal high-voltage fuses and load-break switches

## Slide 337
VOLTAGE-DROP AND POWER-LOSS CALCULATIONS

## Slide 339
Vr
Ir or Is
IR
jIX
IZ
Vs

## Slide 340
Vr
Ir or Is
IR
jIX
IZ
Vs

## Slide 341
a
b
c
n
Vab = √3 Van
S = V I
S = 3 V I
S = √3 V I

## Slide 342
THREE-PHASE BALANCED PRIMARY LINES

## Slide 343
Assume that an overloaded single-phase lateral is to be changed to an equivalent three-phase three-wire and balanced lateral, holding the load constant. Since the power input to the lateral is the same as before,
NON-THREE-PHASE PRIMARY LINES
Single-Phase Two-Wire Laterals with Ungrounded Neutral
Equation (7-1) can be rewritten as
Therefore, from Eq(7-2),

## Slide 344
The voltage drop in the three-phase lateral can be expressed as
and in the single-phase lateral as
where KR and K are conversion constants of R and X and are used to convert them from their three-phase values to the equivalent single-phase values.
Therefore Eq. (7-5) can be rewritten as -

## Slide 345
or substituting Eq. (7-3) into Eq. (7-6),
By dividing Eq. (7-7) by Eq. (7-4) side by side,
Eq. (7-8) can be expressed in per units as
The power losses due to the load currents in the conductors of the single-phase lateral and the equivalent three-phase lateral are

## Slide 346
Substituting Eq. (7-3) into Eq. (7-12)
and dividing the resultant Eq. (7-14) by Eq. (7-13) side by side

## Slide 347
Single-Phase Two-Wire Unigrounded Laterals
In general, this system is presently not used due to the following disadvantages.
There is no earth current in this system. It can be compared to a three-phase four-wire balanced lateral in the following manner.
Since the power input to the lateral is the same as before
from which
The voltage drop in the three-phase lateral can be expressed as

## Slide 348
and in the single-phase lateral as

## Slide 349
The power losses due to the load currents in the conductors of the single-phase two-wire unigrounded lateral with full-capacity neutral and the, equivalent three-phase four-wire balanced lateral are
and
respectively. Substituting Eq. (7-18) into Eq. (7-24),
and dividing Eq. (7-26) by Eq. (7-25) side by side,

## Slide 350
Single-Phase Two-Wire Laterals with Multigrounded Common Neutrals

## Slide 351
According to Morrison [1], the return current in the neutral wire is
In Fig. 7-2, the constant KR is less than 2.0 and the constant K is more or less equal to 2.0 because of conflictingly large Dm (i.e., mutual geometric mean distance or geometric mean radius, GMR) of the Carson’s equivalent ground (neutral) conductor
Therefore, assuming that the data from Morrison [1] are accurate,

## Slide 352
the per unit voltage drops and the power losses due to load currents can be approximated as
Two-Phase Plus Neutral (Open.Wye) Laterals

## Slide 353
Theoretically, it can be expressed that
where
Assuming equal load division among phases, the two-phase plus neutral lateral can be compared to an equivalent three-phase lateral, holding the total kilovoltampere load constant. Therefore

## Slide 354
If the neutral is unigrounded and the neutral-conductor impedance (Zn) is zero, the voltage drop in each phase s
Therefore
or substituting Eq. (7-38) into Eq. (7-40)

## Slide 355
Dividing Eq. (7-41) by Eq. (7-19), side by side
However, if the neutral is unigrounded and the neutral-conductor impedance (Zn) is larger than zero
However, if the neutral is multigrounded and Z > 0, the data from Morrison [1] indicate that the per unit voltage drop in each phase is

## Slide 356
when a full-capacity neutral is used and
The power loss analysis also depends upon whether the neutral is unigrounded or multigrounded. If the neutral is unigrounded, the power loss is

## Slide 357
Based on the data from Morrison [1], the approximate value of this ratio is

## Slide 358
FOUR-WIRE. MULTIGROUNDED COMMON-NEUTRAL DISTRIBUTION SYSTEM

## Slide 366
Thus the total kilovoltampere output of the distribution transformer is
Hence, the load power factor of the distribution transformer is

## Slide 367
PERCENT POWER (OR COPPER) LOSS
The percent power (or conductor) loss of a circuit can be expressed as
At times, in ac circuits, the ratio of percent power, or conductor, loss to percent voltage regulation can be used, and it is given by the following approximate expression:

## Slide 368
METHOD TO ANALYZE DISTRIBUTION FEEDER COSTS
The cost analysis for each feeder-size should include
(1) investment cost of the installed feeder
(2) cost of energy lost due to PR losses in the feeder conductors, and
(3) cost of demand lost, i.e., the Cost of useful system capacity lost (including generation, transmission, and distribution systems)
The total annual feeder cost of a given size feeder can be expressed as

## Slide 369
Annual Equivalent of Investment Cost
Annual Equivalent of Energy Cost

## Slide 370
The load-location factor of a feeder with uniformly distributed load can be defined as
The loss factor can be defined as the ratio of the average annual power loss to the peak annual power loss and can be found approximately for urban areas from
and for rural areas [6]

## Slide 371
Annual Equivalent of Demand Cost
The annual equivalent of demand cost incurred to maintain adequate system capacity to supply the 12R losses in the feeder conductors can be expressed as
The reserve factor is the ratio of total generation capability to the total load and losses to be supplied. The peak-responsibility factor is a per unit value of the peak feeder losses that are coincident with the system peak demand

## Slide 372
Levelized Annual Cost
In general, the costs of energy and demand and even O&M expenses vary from year to year during a given time, as shown in Fig. 7-16a;
Therefore it becomes necessary to levelize these costs over the expected economic life of the feeder, as shown in Fig. 7-16b.
Assume that the costs occur discretely at the end of each year, as shown in Fig. 7-16a. The levelized annual cost of equal amounts can be calculated as
The levelized annual cost of equal amounts can be calculated as
or

## Slide 374
The single-payment discount factor and the capital-recovery factor can be found from the compounded-interest tables or from the following equations, respectively

## Slide 375
ECONOMIC ANALYSIS OF EQUIPMENT LOSSES
Today, the substantially escalating plant, equipment, energy, and capital costs make it increasingly more important to evaluate losses of electric equipment (e.g., power or distribution transformers) before making any final decision for purchasing new equipment and/or replacing (or retiring) existing ones.
For example, nowadays it is not uncommon to find out that a transformer with lower losses but higher initial price tag is less expensive than the one with higher losses but lower initial price when total cost over the life of the transformer is considered.
However, in the replacement or retirement decisions, the associated cost savings in operating and maintehance costs in a given life-cycle analysist or life- cycle cost study must be greater than the total purchase price of the more-efficient replacement transformer.
Based on the “sunk cost” concept of engineering economy, the carrying charges of the existing equipment do not affect the retirement decision, regardless of the age of the existing unit.
In other words, the fixed, or carrying, charges of an existing equipment must be amortized (written ofi) whether the unit is retired or not.

## Slide 376
The transformer cost study should include the following factors:
1. Annual cost of copper losses
2. Annual cost of core losses
3. Annual cost of exciting current
4. Annual cost of regulation
5. Annual cost of fixed charges on the first cost of the installed equipment
Dodds [10] summarizes the economic evaluation of the cost of losses in an old and a new transformer step by step as:
Determine the power ratings for the transformers as well as the peak and average system loads
Obtain the load and no-load losses for the transformers under rated conditions
Determine the original cost of the old transformer and the purchase price of the new one
Obtain the carrying charge rate, system capital cost rate, and energy cost rate for your particular utility
Calculate the transformer carrying charge and the cost of losses for each transformer. The cost of losses is equal to the system carrying charge plus the energy charge

## Slide 377
Compare the total cost per year for each transformer. The total cost is equal to the sum of the transformer carrying charge and the cost of losses
Compare the total cost per year of the old and the new transformer. If the total cost per year of the new transformer is less, replacement of the old transformer can be economically justified

## Slide 383
DISTRIBUTION SYSTEM VOLTAGE REGULATION

## Slide 384
BASIC DEFINITIONS
Voltage regulation: the percent voltage drop of a line (e.g., a feeder) with respect to the receiving-end voltage. Therefore
Voltage drop: the difference between the sending-end and the receiving-end voltages of a line
Nominal voltage: the nominal value assigned to a line or aparatus or a system of a given voltage class
Rated voltage: the voltage at which performance and operating characteristics of apparatus are referred
Service voltage: the voltage measured at the ends of the service-entrance apparatus
Service voltage: the voltage measured at the ends of the service-entrance apparatus

## Slide 385
Utilization voltage: the voltage measured at the ends of an apparatus
Base voltage: the reference voltage, usually 120 V
Maximum voltage: the largest 5-mm average voltage
Voltage spread: the difference between the maximum and minimum voltages, without voltage dips due to motor starting
Minimum voltage: the smallest 5-mm voltage

## Slide 386
QUALITY OF SERVICE AND VOLTAGE STANDARDS
Performance of distribution systems and quality of the service provided are measured in terms of freedom from interruptions and maintenance of satisfactory voltage levels at the customer’s premises that is within limits appropriate for this type of service
The nominal voltage standards for a majority of the electric utilities in the United States to serve residential and commercial customers are
1. 120/240-V three-wire single-phase 2. 240/120-V four-wire three-phase delta 3. 208Y/120-V four-wire three-phase wye 4. 480Y/277-V four-wire three-phase wye
1. 220/380-V two-wire single-phase

## Slide 388
Table 9-1 Typical secondary voltage standards applicable to residential and commercial customers

## Slide 389
As can be observed in Table 9-1, for any given nominal voltage level, the actual operating values can vary over a large range.
This range has been segmented into three zones, namely
(1) the favorable zone or preferred zone
(2) the tolerable zone, and
(3) the extreme zone

## Slide 390
There are numerous ways to improve the distribution system’s overall voltage regulation
VOLTAGE CONTROL
1. Use of generator voltage regulators
2. Application of voltage-regulating equipment in the distribution substations
3. Application of capacitors in the distribution substation
4. Balancing of the loads on the primary feeders
5. Increasing of feeder conductor size

## Slide 391
6. Changing of feeder sections ‘from single-phase to multiphase
7. Transferring of loads to new feeders
8. Installing of new substations and primary feeders
9. Increasing of primary voltage level
10. Application of voltage regulators out on the primary feeders
11. Application of shunt capacitors on the primary feeders
12. Application of series capacitors on the primary feeders

## Slide 392
FEEDER VOLTAGE REGULATORS
Feeder voltage regulators are used extensively to regulate the voltage of each feeder separately to maintain a reasonable constant voltage at the point of utilization
They are either the induction type or the step type
Step-type voltage regulators can be either :
(1) station-type, which can be single- or three-phase, and which can be used in substations for bus voltage regulation or individual feeder voltage regulation
(2) distribution-type, which can be only single-phase and used pole-mounted out on overhead primary feeders
A step-type voltage regulator is fundamentally an autotransformer with many taps (or steps) in the series winding.
Most regulators are designed to correct the line voltage from 10 percent boost to 10 percent buck (that is, ± 10 percent) in 32 steps

## Slide 394
LINE-DROP COMPENSATION

## Slide 395
VOLTAGE FLUCTUATIONS
In general, voltage fluctuations and lamp flicker on distribution systems are caused by a customer’s utilization apparatus.
Lamp flicker can be defined as a sudden change in the intensity of illumination due to an associated abrupt change in the voltage across the lamp.
Most flickers are caused by the starting of motors.
The large momentary inrush of starting current creates a sudden dip in the illuminat ion level provided by incandescent and/or fluorescent lamps since the illumination is a function of voltage.
The annoyance created by lamp flicker is a very subjective matter and differs from person to person.
However, in certain cases, the flicker can be very objectionable and can create great discomfort.
In general, the degree of objection to lamp flicker is a function of the frequency of its occurrence and the rate of change of the voltage dip.
The voltage changes resulting in lamp flicker can be either cyclic or noncyclic in nature. Usually, cyclic flicker is more objectionable.

## Slide 397
Flicker due to motor starting can be reduced by the following remedies:
1. Using a motor which requires less kilovoltamperes per horsepower to start.
2. Choosing a low-starting-torque motor if the motor starts under light load.
3. Replacing the large-size motor with a smaller-size motor or motors.
4. Employing motor starters to reduce the motor inrush current at the start.
5. Using shunt or series capacitors to correct the power factor.
Distribution engineers try every reasonable means to satisfy the motor-start flicker requirement.
After exhausting other alternatives, they may choose to satisfy the flicker condition by installing shunt or series capacitors.

## Slide 398
Shortcut Method to Calculate the Voltage Dips due to a Single-Phase Motor Start
If the starting kilovoltamperage of a single-phase motor is known, the motor’s starting current can be found as
and the voltage dip based on 120 V can be calculated from
where

## Slide 399
Shortcut Method to Calculate the Voltage Dips due to a Three-Phase Motor Start
If the starting kilovoltamperes of a three-phase motor is known, its starting current can be found as
and the voltage dip based on 120 V can be calculated from
where
Substituting Eqs. (9-50) and (9-52) into Eq. (9-5 1), the voltage dip can be expressed as

## Slide 400
REFERENCES
Westinghouse Electric Corporation: Electric Utility Engineering Reference Book—Distribution Systems, vol. 3, East Pittsburgh, Pa., 1965.
Voltage Raringsfor Electric Power Systems and Equipment, American National Standards Institute ANSI C84.1-1977
McCrary, M. R.: “Regulating Voltage on a Major Power System,” The Line, vol. 81, no.’1, 1981, pp.2—8.
Hopkinson, R. H.: “Recap S Computer Program Aids Voltage Regulation Studies.” E(ectr. Forum. vol. 4, no. 4, 1978, pp.20—23.
Fink, D. G., and H. W. Beaty: Standard Handbookfor Electrical Engineers, 11th ed., McGraw-Hill, New York, 1978.
Oklahoma Gas and Electric Company: Engineering Guides, Oklahoma City, January 1981.
Gónen, T., et al.: Development of Advanced Methods for Planning Electric Energy Distribution Systems, U.S. Department of Energy, October 1979. Available from the National Technical Information Service, U.S. Department of Commerce, Springfield, Va
Bovenizer, W. N.: “New. ‘Simplified’ Regulator for Lower-Cost Distribution Voltage Regulation,” The Line, vol. 75, no. 1, 1975, pp. 25—28.
W. N.: “Paralleling Voltage Regulatois,” The Line, vol. 75, no. 2, 1975, pp.6—9.

## Slide 401
Sealey, W. C.: “Increased Current Ratings for Step Regulators,” AJEE Trans., pt. III, August 1955, pp. 737—742.
Lokay, H. E., and D. N. Reps: “Distribution System Primary-Feeder Voltage Control: Part I—A New Approach Using the Digital Computer,” AJEE Trans., pt. III, October 1958, pp. 845—855.
Reps, D. N., and G. J. Kirk, Jr.: “Distribution System Primary-Feeder Voltage Control: Part IT—Digital Computer Program,” AJEE Trans., pt. III, October 1958, pp. 856—865.
Amchin, H. K., R. 3. Bentzel, and D. N. Reps: “Distribution System Primary-Feeder Voltage Control: Part Ill—Computer Program Application,” AJEE Trans., pt. III, October 1958, PP. 865—879.
Reps, D. N., and R. F. Cook: “Distribution System Primary-Feeder Voltage Control: Part TV—A Supplementary Computer Program for Main-Circuit Analysis,” AJEE Trans., pt. III, October 1958, pp. 904—913.
Chang, N. E.: “Locating Shunt Capacitors on Primary Feeder for Voltage Control and Loss Reduction,” IEEE Trans. Power Appar. Syst., vol. PAS-88, no. 10, October 1969, pp. 1574—77.
Gônen, T., and F. Djavashi: “Optimum Shunt Capacitor Allocation on Primary Feeders,” IEEE MEXICOtV-8O International Conference, Mexico City, October 22—25, 1980.
Ku, W. S.: “Economic Comparison of Switched Capacitors and Voltage Regulators for System Voltage Control,” AJEE Trans., pt. III, December 1957, pp. 891—906.
Gönen, T., and F. Djavashi: “Optimum Loss Reduction from Capacitors Installed on Primary Feeders,” The Midwest Power Symposium, Purdue University, West Lafayette, md., October 27—28, 1980.

## Slide 417
TERIMAKASIH